| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 1: From duty to ṁ, QH, compressor power, COP

Design target, cooling duty Q̇L = 18 kW for an R134a system. Use the following p–h chart readings (already extracted):

h₁ = 398 kJ/kg, h₂ = 432 kJ/kg, h₃ = 250 kJ/kg, h₄ = 250 kJ/kg.  p₁ = 320 kPa abs, p₂ = 1100 kPa abs.  v₁ = 0.080 m³/kg.

Questions

1) Calculate RE, W, QH, COP.

2) Calculate ṁ to meet 18 kW, then calculate compressor power P and total heat rejected Q̇H.

3) Report heating capacity (condenser heat rejection rate) and pressure ratio. Comment on whether your COP and ratio are consistent (qualitative).

Extension task

If useful superheat at evaporator exit is increased by 5 K, so h₁ rises to 402 kJ/kg (others unchanged), recalculate RE, ṁ, COP and state the trade‑off (capacity vs. discharge temperature).