| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 2: Mass flow to compressor swept volume

- Vapour Compression System – Components

Given (from p–h/tables for an R134a medium‑temp system):

h₁ = 401 kJ/kg, h₂ = 437 kJ/kg, h₄ = 251 kJ/kg, p₁ = 310 kPa abs, p₂ = 1050 kPa abs, v₁ = 0.083 m³/kg.

Compressor: single‑stage reciprocating, ηv = 0.78, speed N = 1450 rpm (one cylinder for this exercise). Load QL = 15 kW.

1) Calculate RE and ṁ.

2) Calculate required swept volume flow V̇s ≈ ṁ·v₁/ηv (m³/s) and the displacement per revolution Vrev = V̇s / (N/60) (m³/rev).

3) Report compression ratio r.

4) Assuming k = 1.12 for superheated vapour, estimate discharge temperature via T₂ ≈ T₁·r{(k−1)/k} with T₁ = 12 °C at state 1 (convert to K). State assumptions.

Extension task

If volumetric efficiency falls to ηv = 0.72, recalculate V̇s and Vrev.

Explain how valve losses/clearance reduce delivered capacity for the same rpm.