| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

F-gas leak check thresholds (by CO₂e)

≥ 5 tCO₂e

Check at least every 12 months (every 24 months with automatic detection)

≥ 50 tCO₂e

Check at least every 6 months (every 12 months with automatic detection)

≥ 500 tCO₂e

Check at least every 3 months (every 6 months with automatic detection)

Automatic detection required (except certain legacy switchgear/ORC)

Task 1 K1.2 Fluids – Refrigerant recovery & F‑gas maths

Use the leak‑check threshold diagram to answer Q1–Q2. Show your working.

1. 8.0 kg of R410A. Using thresholds (5 tCO₂e ≈ 2.4 kg; 50 ≈ 24 kg; 500 ≈ 240 kg for R410A):
a) Which CO₂e band?
b) Minimum leak‑check frequency and change with automatic detection?

2. 110 kg of R404A (thresholds: 5 ≈ 1.3 kg; 50 ≈ 13 kg; 500 ≈ 127 kg).
a) Which band?
b) Is automatic leak detection mandatory?
c) Minimum interval without and with detection?

3. Cylinder weighing. TARE 16.0 kg; MAX GROSS 38.0 kg.
a) Max net refrigerant mass?
b) Live reading is 33.6 kg—how much more can be safely recovered?

4. Routing:

(i) clean R410A from a repair → RE‑USE/RECLAIM/DESTRUCT?

(ii) mixed/contaminated → ?

(iii) scrapped unit with local reclaim available → ?

Extension tasks

CO₂e calculate. Use GWPs: R410A=2088, R134a=1430, R404A=3922.

(a) 6.5 kg R134a → tCO₂e & band

(b) 28 kg R410A → tCO₂e & band

(c) 90 kg R404A → tCO₂e & is detection mandatory?