| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 1: K1.5 Performance parameters for running a refrigeration cycle

Measuring superheat and subcooling

Task 1: Probe placement & calculations (tick/circle and write values)

(a) Circle the two correct probe locations for each measurement on the diagram above and write a one-line reason:

1) Tsuc (suction) for superheat.

Reason:

2) Tliq (liquid line) for subcooling.

Reason:

(b) Convert Psuction and Pdischarge to Tsat(evap) and Tsat(cond) using an appropriate PT chart (provided by your centre).

(c) Calculate: Superheat = Tsuc − Tsat(evap); Subcool = Tsat(cond) − Tliq (show your working).

Task 2: Target ranges by application (short answer)

Write typical target ranges and why they differ: medium-temp cases (~10 K SH), low-temp (~5 K SH), and typical subcool ranges (state assumptions).

Task 3: SOP drafting (bullet points)

Draft a step-by-step SOP (8–12 bullets) covering: meter zero/compensation, probe placement, stabilisation time, safety (A2L/HC awareness), leak-free access (low-loss fittings), recording, and acceptance criteria.

Task 4: Record sheet (complete the blanks)

Use the template below to complete one full line for a chilled room (~3°C) system.

| Date/Time | App | P_suc (bar g) | P_dis (bar g) | T_suc (°C) | T_liq (°C) | SH (K) | SC (K) | Pass/Action |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |

Extension task

Write a one-paragraph note for the client explaining how correct SH/SC helps compressor protection, capacity, and energy efficiency. Link to keeping SST as high and SCT as low as the application allows.