| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 1: Electric Defrost: Heater Sizing, Time & Energy

Scenario

A medium‑temp walk‑in (+3 °C) uses electric defrost. Per cycle, frost mass on the coil is 1.8 kg at 0 °C. The evaporator metal (20 kg, c = 0.90 kJ/kg/K) is at −10 °C at the start of defrost. Heaters warm the coil to +5 °C at termination. Latent heat of fusion of ice = 334 kJ/kg.

Questions

1) Calculate the minimum energy (kJ) to

(a) warm the metal from −10→+5 °C,

(b) melt the 1.8 kg frost,

(c) raise meltwater from 0→+5 °C (cwater = 4.18 kJ/kg/K). Give the total.

2) If heaters deliver 120% of that energy in 20 minutes, find the required kW. Then estimate daily kWh for 4 defrosts/day.

3) Operations trims time‑at‑heat by 25% while keeping drip (3 min) and fan‑delay (4 min) unchanged.

(a) New defrost event time?

(b) New daily kWh?

(c) % energy saving vs. Q2?

Extension task

A defrost termination/fan‑delay control uses 55 °F (≈13 °C) termination & 22 °F (≈−6 °C) fan restart. If the coil cools at 0.6 K/min post‑heat, estimate fan‑delay time.