| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 2: Defrost Controls, Sequences & Compliance

1. Sequence timeline

Draw an electric‑defrost timeline: pump‑down/stop, heaters ON, temperature termination, drip, fan‑delay. Add your centre’s typical termination & fan‑restart temps.

2. Reverse‑flow controls

Explain why a defrost differential is required for gas defrost (reverse flow).

State which header pressure must be higher and give two valve locations commonly used to create/hold the differential.

3. Commissioning checklist

Fill in the blanks for an MT case:

- defrosts/day: ____

- Temperature termination sensor position: ______

- Fail‑safe time: ____ min

- Drip time: ____ min

- Fan‑delay restart: ____ °C

- Differential valve set: ____ kPa (or ____ psi)

- Over‑long defrost alarm: ON/OFF

- Baseline log after week 1: YES/NO

4. Log interpretation

Observed: defrosts end by fail‑safe often; case temperature spikes; fans start immediately at termination. Give two causes and one corrective action for each.

5. Safety & compliance

Before service: isolate heaters; beware hot surfaces/steam; confirm pressure‑relief path; verify valve actuation sequence for gas defrost; ensure drains/pans are clear. Add one site‑specific risk.

Extension task

Write a 6–8 sentence client note: why defrost is required, how frost harms heat transfer & airflow, and how correct initiation/termination avoids wasted energy and temperature excursions.