## Slide 1
Occupational Specialism: Refrigeration Engineering
K1.5: Performance parameters for a running refrigeration system
PowerPoint 1.5

## Slide 2: Introduction
What types of refrigeration systems have you worked on?
Which refrigerant gases have you come across?
In what setting did you work? Commercial, Industrial…?

## Slide 3: Objectives
You should be able to:
Recall different types of refrigeration systems.
Explain the running parameters of those systems.
You might also be able to:
Explain optimising system parameters to ensure an efficient running system.
Explain, select and justify the types of systems and refrigerants based on the application required.

## Slide 4: Chilled storage (3ºC)
Chilled storage should maintain a temperature between: 2ºC and 5ºC.
Max chilled storage temperature is 8ºC.
Should the storage temperature exceed the maximum storage temperature, the product will be rendered waste after a one-time maximum duration of 2 hours.

## Slide 5: Chilled storage (3ºC)
Bacterial growth and enzymatic activity are enemies of food storage; they are processes that occur as the product deteriorates naturally.
The purpose of chilled storage for food products is to store the product above freezing, which may damage the cell structure of the product, but at a temperature that will slow bacterial growth and enzymatic activity, so not affecting the quality, texture, colour, and flavour.

## Slide 6: Chilled storage (3ºC)
Chilled storage is ideal for:
Fresh meat and poultry
Dairy products
Prepared food
Ready-to-eat products

## Slide 7: Blast chilling (3ºC)
Blast chilling and Chilled storage are not the same thing.
Blast chilling is used to bring a product temperature down rapidly, within 90mins.
Bacteria multiplies fastest between 8ºC – 68ºC.
Once the temperature is below 5ºC then the product can be moved to chilled storage.
Blast chillers are generally used in commercial kitchens and food processing facilities.

## Slide 8: Blast chilling (3ºC)
According to the Journal of Food Science, reduces bacteria growth by up to 98%.
Extends shelf life.
Energy efficient, uses 25% less energy/kg of product in 90 mins compared to 4-6 hours in standard refrigerators.

## Slide 9: Blast chilling (3ºC) performance parameters
Suction pressure/saturated suction temp:
-5ºC to -10ºC SST
Superheat:
4–8 K at evaporator outlet
Subcooling:
3–5 K at condenser outlet / receiver
Running currents:
Within nameplate FLC at design load
Discharge pressure/saturated discharge temp:
30ºC - 40ºC (ambient dependent)

## Slide 10: Refrigerant options
Industrial
NH₃ or CO₂
Commercial
HFO / HFC

## Slide 11: Cold storage (-20ºC)
Conventional cold storage should maintain a temperature between:
-18ºC and -30ºC
The process of conventional freezing is temperature reduction over an extended time frame; the product enters cold storage after a chilling process and is then left to drop to the desired storage temperature, which it will be held at for long-term storage.

## Slide 12: Cold storage (-20ºC)
Conventional freezing techniques, where the product temperature cools slowly, damage cell structures and affect the overall product quality.
The slow freeze process allows for large ice crystals to form, which can break the structure/texture of the product. Fresh fruits turn mushy, and meat loses its texture after defrosting.

## Slide 13: Cold storage (-20ºC)
Cold storage is ideal for:
Fresh meat and poultry
Dairy products
Seafood
Frozen vegetables
Ready meals.

## Slide 14: Cold storage (-20ºC)
Pharmaceuticals: Storage of vaccines, biological samples and reagents for scientific discovery and practical laboratory work.
Cold chain distribution centres and logistics.
Warehousing for frozen goods.
Industrial: Cold chain distribution and centres.

## Slide 15: Cold storage (-20ºC)
Product quality loss occurs when frozen over long term durations due to large ice crystal formation, which leads to cell damage in terms of texture colour and flavour.
Extends standard shelf life. Freezing halts bacterial and microbial growth but does not stop it.
Cost effective.

## Slide 16: Meat storage time limits based on product quality
Process step / item | Hazard controlled | Critical limits (Time/Temp) | Max holding time (Quality)
Raw beef/veal/lamb/pork – steaks, chops, roasts | Quality loss (freezer burn, oxidation) | ≤ –18 °C continuous | 4–12 months
Raw ground meat / minced meat | Quality loss (fat oxidation) | ≤ –18 °C | 3–4 months
Bacon & sausage (frozen) | Quality loss (freezer burn, oxidation) | ≤ –18 °C | 1–2 months
Cooked meat (meat dishes / cooked meat) | Quality loss | ≤ –18 °C | 2–3 months

## Slide 17: Cold storage (-20ºC) Performance Parameters:
Suction pressure/saturated suction temp:
-28ºC to -40ºC SST
Superheat:
4-8 K at evaporator outlet
Subcooling:
Sufficient to avoid flash gas at expansion valve
Running currents:
Close to FLC at design load
Discharge pressure/saturated discharge temp:
30ºC - 40ºC (ambient dependent)

## Slide 18: Refrigerant options
Industrial
NH₃ or CO₂
Commercial
HFO / HFC

## Slide 19: Blast freezing (-40ºC)
Although the speed of freezing requires a large amount of energy usage over a short period it reduces extended operation and product wastage. Energy efficiency is increased over the long term.
Extends standard shelf life. Freezing halts bacterial and microbial growth but does not stop it.
The speed of freezing prevents large ice crystals forming so is ideal for delicate products.
The increased speed of the freezing duration preserves products at peak quality for longer.

## Slide 20: Blast freezing (-40ºC)
Increased initial costs over conventional freezing methods.
Larger footprint required, reducing production area.

## Slide 21: Blast freezing (-40ºC)
Pharmaceuticals
Industrial food production
Restaurants

## Slide 22: Blast freezing (-40ºC)
Blast freezing is ideal for:
Fresh meat and poultry
Seafood
Frozen vegetables
Baked goods
Fruit and other delicates.

## Slide 23: Blast freezing (-40C) methods
Air blast individual quick freezing (IQF)
often called ‘flash freezing’.
Spiral blast freezers (belt freezing) + fluidised bed freezing.
IQF Tunnels.
Plate freezing, Immersion freezing - brine freezing and cryogenic freezing.

## Slide 24: Air blast Individual quick-freezing (IQF) (-40ºC)
The success of the individual quick-freezing method relies on the speed and separation of each piece of product; each item is individually frozen.
Product is first prepared, washed, trimmed, sized, and moisture controlled using air, to ensure uniform freezing.
The product is then passed through either a tunnel IQF, spiral IQF or a fluidized bed IQF.
Notes: Provide

## Slide 25: Tunnel IQF (-40ºC)
Air at very low temperatures (-40ºC) is circulated at high speeds up to 3m/s.
Ensuring that freezing through the critical -1ºC to -4ºC range is quick.
Prevents large ice crystals forming and so preserves the quality of the product.
Notes: Provide

## Slide 26: Spiral freezing (-40ºC)
A spiral IQF employs a conveyor belt system that is constructed in a vertical spiral tower configuration, the conveyor belt wrapping around a central drive tower. Allowing high volume production due to the compact footprint.
Can be single or double spiral configuration.
Product enters at the bottom and exits at the top.
Air flow can be counter-current to the belt direction or from the top and bottom.
Notes: Provide

## Slide 27: Fluidised bed freezing (-40ºC)
Used primarily in the food industry.
Product is moved by linear perforated conveyor belt and is suspended in the upward direction cold air stream. Produce appears to float, this is where the name is derived from.
The freezing occurs quickly, used for small product, prevents clumping and maintains excellent product quality.
High Efficiency slowing for continuous high-volume production.
Notes: Provide

## Slide 28: Plate freezing (-40ºC)
The plates are vertical or horizontal configuration.
Vertical plates allow product to be poured between the plates this allows no air to be trapped and so increases quality and reduces wastage.
Horizontal plates and multi level plates allow for high volume production.
Double contact is one of the fastest freezing methods.
Notes: Provide

## Slide 29: Brine freezing (-40ºC)
Brine Freezing: Food product is submerged in or sprayed with a low temperature brine solution. Brine is a secondary refrigerant, cooled by tank or low temp liquid chillers.
Widely used in food processing, especially useful in seafood, meat and diary products. Care must be taken to ensure the product is not adversely tainted if the brine concentration is too high, salinity concentrations are between 3-23%.
The brine is continuously agitated to ensure an even freezing process. Brine freezing can be conveyor feed or tray feed. Provides a balance between speed and cost effectiveness.

## Slide 30: Cryogenic freezing (-40ºC)
Cryopreservation: Cryogenic freezing, freezes biological products to -196ºC using Liquid nitrogen. Liquid nitrogen is sprayed or injected into a tunnel; the nitrogen boils instantly when it touches the warm food, and vitrification occurs, turning the product into a glass-like solid state. The process is the fastest method of freezing but is expensive. Used for high volumetric efficiency and heat-sensitive products.
CO2 freezing is another example of cryogenic freezing. CO2 at -79ºC is injected into the freezer space, the CO2 sublimates, so it leaves no trace on the product. A slower freeze than Nitrogen but also a cheaper option. Used within the food industry.
In real terms neither of these methods are true refrigeration cycles but they are methods of Individual quick-freezing products used in varying industries. Both methods have additional costs of ventilation. With the CO2 method also adding a CO2 gas load to the environment when vented.

## Slide 31
Method | Freezing rate | Cost | Applications | Advantages | Disadvantages
Air Blast Freezing | Slow to moderate | Low | Various packaged foods, vegetables, meat | Versatile, cost-effective | Slower freezing, potential for larger ice crystals
Plate freezing | Moderate to fast | Moderate | Uniformly shaped products, fish fillets, meat patties | Efficient heat transfer, uniform freezing | Limited to specific shapes
Brine freezing | Fast | Moderate | Fish, poultry | Rapid freezing | Potential for salt absorption
Cryogenic freezing (LN2) | Very fast | High | Delicate foods, fruits, seafood | Ultra-rapid freezing, superior quality | High cost, specialized equipment
Cryogenic freezing (CO2) | Fast | Moderate to high | Meat, poultry, baked goods | Rapid freezing, good quality | Higher cost than air blast

## Slide 32: Blast freezing (-40ºC) performance parameters
Suction pressure/saturated suction temp:
-28ºC to -40ºC SST
Superheat:
4-8 K at evaporator outlet
Subcooling:
Sufficient to avoid flash gas at expansion valve
Running currents:
Close to FLC at design load
Discharge pressure/saturated discharge temp:
30ºC - 40ºC (ambient dependent)

## Slide 33: Refrigerant options
Industrial
NH₃ / CO₂ cascade
Commercial
HFO / HFC
NH₃ / CO₂ cascade

## Slide 34: Liquid chillers
Liquid chillers use a refrigeration cycle to cool a secondary heat transfer fluid which is then circulated via pumps to the process equipment.
Chillers contain the same core components as any other refrigeration system and can be either water or air cooled.
Compressor selection is based around application. The table on the next slide provides: application - refrigerant - compressor type.

## Slide 35
Temperature | Primary refrigerants | Secondary refrigerant | Compressor types | Typical applications
High-temp | R134a, R513A, R1234ze, R410A (phasing down) | Water/ glycol (low concentrations) | Scroll, Screw, Centrifugal | HVAC chillers, comfort cooling
Medium‑temp | R449A, R448A, R454A/C, R455A, CO₂ | Propylene Glycol Ethylene Glycol Brines | Reciprocating, Screw, CO₂ transcritical | Supermarkets, process cooling
Low‑temp | R452A, R404A (legacy), CO₂, R717 | High concentration Glycols Calcium Chloride or Potassium Formate Brines Specialised Low temp Heat transfer fluids | Two‑stage recip, Screw, Cascade | Freezers, blast chillers, industrial LT

## Slide 36: Liquid chillers
Liquid chillers offer:
Reduced primary refrigerant charge
Improved food safety
Centralised refrigeration plants
No refrigerant in process areas
Simple maintenance and expansion potential.

## Slide 37: Liquid chillers
High Temperature: Chilled storage (3ºC), process cooling, HVAC, blast chillers.
Medium: Chilled water for meat, fish, and dairy processing. Cooling jackets and plate heat exchangers.
Low temperature applications: IQF tunnels and spiral freezers, cold storage and industrial freezing processes.

## Slide 38: Liquid chillers - advantages
Only the chiller contains refrigerant, no refrigerant in occupied spaces.
Lower leak potential.
Long fluid pipework runs avoid oil return issues, reduce pressure drop issues.
Future proof against F gas phase-downs with reduced F gas compliance.
Ideal for ammonia chillers, CO2 chillers or A2L chillers.
Secondary refrigerants have high thermal mass.
Stable uniform temperature delivery.

## Slide 39: Liquid chillers - disadvantages
Lower efficiency. Lower COP.
Pump power requirements adds significant energy usage.
Fluid degradation, decrease in glycol concentration over time.
Large footprint required, Bigger heat exchangers, larger pipes.
Higher initial installation costs.
Increased maintenance and fluid testing on the fluid side.
Potential for bacterial growth.
More complex fluid side design.

## Slide 40: Liquid chillers performance parameters
Suction pressure/saturated suction temp:
-28ºC to -40ºC SST
Superheat:
4-8 K at evaporator outlet
Subcooling:
Sufficient to avoid flash gas at expansion valve
Running currents:
Close to FLC at design load
Discharge pressure/saturated discharge temp:
30ºC - 40ºC (ambient dependent)

## Slide 41: Summary
Category | Typical Range | Purpose
Chilled storage | 0°C to 10°C | Fresh produce, dairy
Medium‑low | 0°C to –18°C | Seafood, meats, general frozen goods
Low / Freezer storage | –18°C to –30°C | Long‑term frozen storage
Ultra‑low | –40°C to –60°C | Biological samples, specialised pharma

## Slide 42: Summary of refrigeration systems and refrigerants
Application | Temperature Range | System Type | Preferred Refrigerants
Chilled storage | ≈3°C | Cold room | NH₃, HFO
Blast chilling | Pull‑down to 3°C | Blast chiller | NH₃, HFO
Medium‑temp processing | 0°C to –10°C | Liquid chiller | NH₃, CO₂
Blast freezing | ≤ –18°C | Blast freezer | NH₃, NH₃/CO₂
IQF freezing | –18°C to –40°C | IQF tunnel/spiral | NH₃, CO₂ cascade
Spiral freezing | –25°C to –40°C | Spiral freezer | NH₃, CO₂ cascade
Frozen storage | –20°C | Cold store | NH₃, NH₃/CO₂

## Slide 43: Summary
You should be able to:
Recall different types of refrigeration systems.
Explain the running parameters of those systems.
You might also be able to:
Explain optimising system parameters to ensure an efficient running system.
Explain, select and justify the types of systems and refrigerants based on the application required.

## Slide 44
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.