| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 2: Mass flow to compressor swept volume

- Vapour Compression System – Components

Given (from p–h/tables for an R134a medium‑temp system):

h₁ = 401 kJ/kg, h₂ = 437 kJ/kg, h₄ = 251 kJ/kg, p₁ = 310 kPa abs, p₂ = 1050 kPa abs, v₁ = 0.083 m³/kg.

Compressor: single‑stage reciprocating, ηv = 0.78, speed N = 1450 rpm (one cylinder for this exercise). Load QL = 15 kW.

1) Calculate RE and ṁ.

2) Calculate required swept volume flow V̇s ≈ ṁ·v₁/ηv (m³/s) and the displacement per revolution Vrev = V̇s / (N/60) (m³/rev).

3) Report compression ratio r.

4) Assuming k = 1.12 for superheated vapour, estimate discharge temperature via T₂ ≈ T₁·r{(k−1)/k} with T₁ = 12 °C at state 1 (convert to K). State assumptions.

Extension task

If volumetric efficiency falls to ηv = 0.72, recalculate V̇s and Vrev.

Explain how valve losses/clearance reduce delivered capacity for the same rpm.

Tutor guidance

Answers

Question 1

RE= h1 −h4 =401−251 = 150.0 kJ/kg;

ṁ=Q̇L/RE=15.0/150.0=0.100 kg/s.

Question 2

V̇s ≈ ṁ·v₁/ηv = 0.100×0.083/0.78 = 0.01064 m³/s

Vrev = V̇s/(N/60) = 0.000440 m³/rev

Question 3

Compression ratio r = p₂/p₁ = 1050/310 = 3.387:1 Compression ratio = 3.39 (approx.)

Question 4

T₂ ≈ T₁·r((k−1)/k) with T₁=285.15 K, k=1.12 → T₂ ≈ 325.0 K (≈ 51.8 °C).

Estimated discharge temperature ≈ 52 °C

This is an estimate (idealised, ignores inefficiencies/pressure drops).

Extension

With ηv=0.72,

V̇s= 0.1 x 0.082/0.72 = 0.01153 m³/s,

Vrev=0.000477 m³/rev

(Higher swept volume required when volumetric efficiency falls.)