| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

F-gas leak check thresholds (by CO₂e)

≥ 5 tCO₂e

Check at least every 12 months (every 24 months with automatic detection)

≥ 50 tCO₂e

Check at least every 6 months (every 12 months with automatic detection)

≥ 500 tCO₂e

Check at least every 3 months (every 6 months with automatic detection)

Automatic detection required (except certain legacy switchgear/ORC)

Task 1 K1.2 Fluids – Refrigerant recovery & F‑gas maths

Use the leak‑check threshold diagram to answer Q1–Q2. Show your working.

1. 8.0 kg of R410A. Using thresholds (5 tCO₂e ≈ 2.4 kg; 50 ≈ 24 kg; 500 ≈ 240 kg for R410A):
a) Which CO₂e band?
b) Minimum leak‑check frequency and change with automatic detection?

2. 110 kg of R404A (thresholds: 5 ≈ 1.3 kg; 50 ≈ 13 kg; 500 ≈ 127 kg).
a) Which band?
b) Is automatic leak detection mandatory?
c) Minimum interval without and with detection?

3. Cylinder weighing. TARE 16.0 kg; MAX GROSS 38.0 kg.
a) Max net refrigerant mass?
b) Live reading is 33.6 kg—how much more can be safely recovered?

4. Routing:

(i) clean R410A from a repair → RE‑USE/RECLAIM/DESTRUCT?

(ii) mixed/contaminated → ?

(iii) scrapped unit with local reclaim available → ?

Extension tasks

CO₂e calculate. Use GWPs: R410A=2088, R134a=1430, R404A=3922.

(a) 6.5 kg R134a → tCO₂e & band

(b) 28 kg R410A → tCO₂e & band

(c) 90 kg R404A → tCO₂e & is detection mandatory?

Tutor guidance

Answers

1a) CO₂e band

8.0 kg lies between 2.4 kg and 24 kg, therefore:

Band: ≥ 5 to < 50 tCO₂e

1b) Leak-check frequency

- 5–50 tCO₂e → every 12 months

- With automatic detection → every 24 months

Minimum frequency: 12 months
With automatic detection: 24 months

2a) CO₂e band

110 kg lies between 13 kg and 127 kg, therefore:

Band: ≥ 50 to < 500 tCO₂e

2b) Is automatic leak detection mandatory?

Mandatory only ≥ 500 tCO₂e, with exceptions for legacy switchgear/ORC.
110 kg is below the 500-tCO₂e threshold.

Automatic leak detection NOT mandatory.

2c) Leak-check frequency

- 50–500 tCO₂e → every 6 months

- With automatic detection → every 12 months

Without detection: 6 months
With detection: 12 months

3a) Max net refrigerant

Max net = MAX GROSS − TARE
= 38.0 − 16.0 = 22.0 kg

Max net refrigerant = 22.0 kg

3b) Live reading = 33.6 kg

Remaining capacity = MAX GROSS − current weight
= 38.0 − 33.6 = 4.4 kg

Can recover a further 4.4 kg safely

4) Routing:

(i) clean R410A from a repair → RE‑USE or RECLAIM

(ii) mixed/contaminated → DESTRUCT

(iii) scrapped unit with local reclaim available → RECLAIM

Extension

(a) 6.5 kg R134a → tCO₂e & band;

tCO₂e = 6.5 × 1430 / 1000 = 9.30 tCO₂e

Band: 9.3 ≥ 5 but < 50 → 5–50 tCO₂e band

9.3 tCO₂e → 5–50 band

(b) 28 kg R410A → tCO₂e & band;

tCO₂e = 28 × 2088 / 1000 = 58.46 tCO₂e

Band: 58.46 ≥ 50 but < 500 → 50–500 tCO₂e

58.46 tCO₂e → 50–500 band

(c) 90 kg R404A → tCO₂e & is detection mandatory?

tCO₂e = 90 × 3922 / 1000 = 352.98 tCO₂e

Band: 352.98 ≥ 50 but < 500 → 50–500 tCO₂e
Mandatory detection? Only ≥ 500 tCO₂e

352.98 tCO₂e → 50–500 band, NOT mandatory