| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 2: K1.5 Performance parameters for running a refrigeration cycle

Refrigerant selection for low/medium/high-temp applications

Task 1: Selection matrix (tick and justify)

For each application below, tick two suitable refrigerants and write 2–3 lines to justify against performance, safety class, and service practicality:

| Application | Options (tick 2) | Safety class | Typical temp band | Why this is suitable (2–3 lines) | Notes |
| --- | --- | --- | --- | --- | --- |
| Low-temp (blast/−40°C air) | R744 (CO2) ☐ R717 (NH3) ☐ R290 (HC) ☐ R404A(legacy) ☐ | A1 / B2L / A3 | Evap ≤ −35°C |  |  |
| Medium-temp (chilled +3°C) | R744 ☐ R134a(legacy) ☐ R513A ☐ R1234ze ☐ R290 ☐ | A1/A2L/A3 | Evap ~ −6…−2°C |  |  |
| High-temp chiller (L/M pressure) | R1234ze ☐ R1233zd ☐ R513A ☐ | A2L/A1 | Evap ≥ 0°C |  |  |
| Secondary loop (glycol/brine) | Primary: R717 ☐ R744 ☐ R290 ☐ HFO ☐ | B2L/A1/A3/A2L | Primary depends on plant |  |  |

Task 2: Safety & compliance note (short answer)

State the safety group for each refrigerant you selected and one implication for installation/servicing (e.g. ventilation, leak detection, charge limits).

Task 3: Efficiency & temperature lift (paragraph)

Explain how your choices support low condensing temperatures and high evaporating temperatures for best COP in the stated application.

Extension task

Retrofit scenario: A medium-temp R134a chiller needs lower GWP. Propose a drop-in or near-drop-in option and list three commissioning checks (oil compatibility, TXV settings/SH, leak-tightness test).

Tutor guidance

Answers

Task 1
Low-temp: R744 widely used in LT packs/IQF; R717 high efficiency in industrial plants (trained staff). R290 in small charges with charge-limit rules.

Medium-temp: R513A or R1234ze for lower GWP vs. R134a; R744 viable in transcritical/booster supermarkets; R290 in small systems.

High-temp chillers (L/M pressure): R1234ze/R1233zd common (very low GWP, good efficiency).

Secondary loops: use R717/R744/R290 primary; circulate glycol/brine to loads.

Task 2
Safety & compliance: State A1/A2L/A3/B2L; mention ventilation, detection, machinery rooms, training, and charge-limit compliance.

Task 3
Efficiency & lift: Choices should enable low SCT and as high SST as product allows; e.g. CO2 with parallel compression/ejectors; ammonia’s strong thermodynamics for large plants.

Extension

Drop-in / Near-drop-in Options for R134a (lower GWP):

- R513A (very common near-drop-in)

- R1234ze (another low-GWP alternative)

Three commissioning checks:

- Check system pressures and superheat/subcooling are within the manufacturer’s recommended range for the new refrigerant.

- Verify refrigerant charge level—adjust if needed due to different glide or density.

- Check for leaks and ensure all labelling and safety documentation reflects the new refrigerant.