| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 3: K1.5 Performance parameters for running a refrigeration cycle

Optimising SST/SCT from an Operations Log (Floating Head/Suction)

Below is a simplified 1-day log for a medium-temp rack. Complete the analysis and propose control changes.

| Time | Box (°C) | SST (°C) | SCT (°C) | kW comp | kW fans/pumps | Notes |
| --- | --- | --- | --- | --- | --- | --- |
| 06:00 | 4.0 | −8 | 31 | 72 | 11 | Cool dawn |
| 10:00 | 3.2 | −7 | 36 | 79 | 12 | Rising ambient |
| 14:00 | 3.1 | −8 | 41 | 88 | 13 | Peak ambient |
| 18:00 | 3.4 | −7 | 37 | 80 | 12 |  |
| 22:00 | 3.6 | −6 | 32 | 73 | 11 | Night |

Task 1:

Where could SCT be floated lower without risking capacity? Where could SST be floated higher? Justify from the log.

Task 2:

Propose: (a) a day/night floating head band (°C vs. ambient) and (b) an SST band that still maintains a 3°C box. State any alarm differentials.

Task 3:

Explain how lowering SCT by about 3 K and/or raising SST by about 2 K affects lift and compressor energy.

Extension

Draft a short ‘floating head/suction’ SOP covering sensor validation, minimum condensing temperature limits (fan control/valves), product-temperature guards, and seasonal recommissioning.

Tutor guidance

Answers

Task 1: Lower SCT at 06:00/22:00 (31–32°C) – head can likely float further down; at 14:00 SCT is high (41°C) – accept higher head. SST could float up slightly at 06:00–10:00/22:00 while box ≤3.6°C.

Task 2: Example band – head: ambient+8…+12 K with minimum 28–30°C; suction: set to hold box 3°C with TD margin (e.g., SST −5…−7°C) and alarm at box >5–6°C.

Task 3: Lowering SCT by ~3 K and/or raising SST by ~2 K reduces temperature lift → lower pressure ratio and compressor kW; COP increases (qualitatively per Carnot).

Extension: SOP should reference sensor checks, condenser fan/VFD or valve sequencing, winter bypass control, data-logging, and revert limits for defrost/peaks.