| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 1: Electric Defrost: Heater Sizing, Time & Energy

Scenario

A medium‑temp walk‑in (+3 °C) uses electric defrost. Per cycle, frost mass on the coil is 1.8 kg at 0 °C. The evaporator metal (20 kg, c = 0.90 kJ/kg/K) is at −10 °C at the start of defrost. Heaters warm the coil to +5 °C  at termination. Latent heat of fusion of ice = 334 kJ/kg.

Questions

1) Calculate the minimum energy (kJ) to

(a) warm the metal from −10→+5 °C,

(b) melt the 1.8 kg frost,

(c) raise meltwater from 0→+5 °C (cwater = 4.18 kJ/kg/K). Give the total.

2) If heaters deliver 120% of that energy in 20 minutes, find the required kW. Then estimate daily kWh for 4 defrosts/day.

3) Operations trims time‑at‑heat by 25% while keeping drip (3 min) and fan‑delay (4 min) unchanged.

(a) New defrost event time?

(b) New daily kWh?

(c) % energy saving vs. Q2?

Extension task

A defrost termination/fan‑delay control uses 55 °F (≈13 °C) termination & 22 °F (≈−6 °C) fan restart. If the coil cools at 0.6 K/min post‑heat, estimate fan‑delay time.










Tutor guidance

Answers

1) Minimum Energy Required

(a) Warm metal from -10 to +5 °C

Qmetal= mcDT = 20 kg × 0.90 × 15 K = 270 kJ

(b) Melt frost (1.8 kg at 0 °C)

Qmelt = mLf = 1.8 × 334 = 601.2 kJ

(c) Heat meltwater from 0 to 5 °C

Qwater = mcDT = 1.8 × 4.18 × 5 = 37.62 kJ

Total minimum energy = 270 + 601.2 + 37.62 = 908.82 kJ

2) Heater Requirement

Heaters supply 120% ® 1.2 × 908.8 = 1090.6 kJ

Heater time = 20 min = 1200 s

Power = 1090.6 / 1200 = 0.91 kW

Daily energy:

Energy per day:

E=4×1090.56=4362.24 kJ

Convert to kWh:

4362.243600=1.2117

1.21 kWh/day

3) Reduced Time-at-Heat (25% reduction)

New heat time = 20 × 0.75 = 15 min

New total = 15 + 3 + 4 = 22 min

New daily energy = 0.91 kWh/day

Savings » 25%

Extension task

Coil cool: 13 to –6 °C ® DT = 19 K

Cooldown rate = 0.6 K/min ® time = 19 / 0.6 » 32 min