| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 2: Defrost Controls, Sequences & Compliance

1. Sequence timeline

Draw an electric‑defrost timeline: pump‑down/stop, heaters ON, temperature termination, drip, fan‑delay. Add your centre’s typical termination & fan‑restart temps.

2. Reverse‑flow controls

Explain why a defrost differential is required for gas defrost (reverse flow).

State which header pressure must be higher and give two valve locations commonly used to create/hold the differential.

3. Commissioning checklist

Fill in the blanks for an MT case:

- defrosts/day: ____

- Temperature termination sensor position: ______

- Fail‑safe time: ____ min

- Drip time: ____ min

- Fan‑delay restart: ____ °C

- Differential valve set: ____ kPa (or ____ psi)

- Over‑long defrost alarm: ON/OFF

- Baseline log after week 1: YES/NO

4. Log interpretation

Observed: defrosts end by fail‑safe often; case temperature spikes; fans start immediately at termination. Give two causes and one corrective action for each.

5. Safety & compliance

Before service: isolate heaters; beware hot surfaces/steam; confirm pressure‑relief path; verify valve actuation sequence for gas defrost; ensure drains/pans are clear. Add one site‑specific risk.

Extension task

Write a 6–8 sentence client note: why defrost is required, how frost harms heat transfer & airflow, and how correct initiation/termination avoids wasted energy and temperature excursions.

Tutor guidance

Answers

1. Sequence timeline

Typical practice: termination often ~40–75 °F (≈4–24 °C); fan restart ~20–24 °F (≈−7 to −4 °C) after drip/dry (centre‑specific).

2. Reverse‑flow controls

A defrost differential is needed so the system knows when to switch into gas defrost and when to stop. It prevents the system from rapidly switching back and forth.

3. Commissioning checklist

- Defrosts/day: 3–4

- Temperature termination sensor position: Evaporator outlet / upper coil return bend

- Fail-safe time: 20–30 min

- Drip time: 3–5 min

- Fan-delay restart: 5–10 °C coil temperature

- Differential valve set: 70–140 kPa (or 10–20 psi)

- Over-long defrost alarm: ON

- Baseline log after week 1: YES

4. Log interpretation

Causes: sensor mis‑placed/failed → no temp termination; insufficient defrost heat (faulty heaters/low gas flow) → incomplete defrost; fan‑delay disabled → warm moist air blown to space. Fix: relocate/replace sensor; repair heaters/valves & adjust differential; enable/extend fan‑delay.

5. Safety & compliance (bullet points)

Safety: isolate heaters; beware hot condensate/steam; confirm valve logic & relief; ensure drains/heated pans operate; include site‑specific hazards.

Extension task

Emphasise frost as thermal resistance & airflow blockage; good controls cut energy & temp spikes; demand‑based initiation can reduce unnecessary cycles.

Example:
Frost naturally forms on evaporator coils whenever moist air enters a refrigerated display or cold room. As frost thickens, it acts as an insulating layer, reducing heat-transfer efficiency and forcing the system to run longer to maintain temperature. It also blocks airflow through the coil, causing warm spots and poor product temperature control. Defrost cycles remove this frost, allowing the system to operate at its intended capacity. When defrost starts and ends at the correct points, it removes only the necessary frost without overheating the case or wasting energy. Temperature-based termination prevents unnecessary heater runtime, while fan delay ensures that residual heat is not blown onto the product. Proper control setup, therefore, keeps energy use low, maintains stable product temperatures, and extends equipment life. Good defrost control is one of the most cost-effective maintenance actions for refrigerated equipment.