| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 3: Off‑Cycle Defrost: Feasibility, Timing & Energy

Scenario

A medium‑temp case holds +4 °C air and runs SST ≈ −6 °C. Off‑cycle defrost is scheduled 6×/day. During off‑cycle, the compressor stops, and the fans run.

Assume

(a) Coil + frost equivalent heat capacity Ceq = 14 kJ/K;

(b) Average air‑to‑coil UA = 65 W/K;

(c) Coil temp at start of defrost = −8 °C;

(d) Melt begins at 0 °C.

Treat the coil as a lumped mass exchanging with room air at +4 °C.

1) Using T(t) = Tr − (Tr − T0)·exp(−(UA/Ceq)·t), calculate the time to reach 0 °C (start of melting). (Convert UA to kJ/s/K.)

2) If mfrost = 0.8 kg, estimate additional time to melt by assuming sensible heat from room air only at an average ΔT of 3 K and the same UA. (Latent of fusion = 334 kJ/kg.)

3) Check feasibility: if total exceeds 10 min, propose a revised frequency (defrosts/day) or off‑cycle duration to fully clear frost without heaters.

Extension task

Suggest a demand‑based initiation strategy using a low‑pressure cut‑out or fan pressure‑differential, with one advantage and one risk.

Tutor guidance

Answers

1) Time to warm coil from -8°C to 0°C:

Given: Tr = 4°C, T0 = -8°C, UA = 65 W/K = 0.065 kJ/s/K, Ceq = 14 kJ/K.

Time constant: τ= Ceq / UA = 14 / 0.065 = 215.38 s.

Solve for t using T(t) = Tr - (Tr - T0)*exp(-(UA/Ceq)*t).

Setting T(t) = 0°C gives t = τ * ln(3) = 236.6 s = ~3.9 min.

2) Time to melt 0.8 kg of frost:

Latent heat required = m * Lf = 0.8 * 334 = 267.2 kJ.

Heat transfer during melting: ΔT = 3 K, UA = 0.065 kJ/s/K.

Q˙ = UA * ΔT = 0.195 kJ/s.

Melt time = 267.2 / 0.195 = 1370 s = 22.8 min.

Total required off-cycle time = 3.9 + 22.8 = 26.7 min.

3) Feasibility:

10-minute off-cycle is insufficient; need ~27 minutes per cycle.

Recommended change: reduce frequency to ~3 defrosts/day.

Demand-based defrost suggestions:

Option A: Low-pressure cut-out for initiation (advantage: adaptive; risk: false triggers).

Option B: Coil pressure-differential sensor (advantage: accurate; risk: sensor maintenance).

If total > 10 min, increase frequency (e.g. 8×/day) or extend off‑cycle window; demand‑based initiation can trim unnecessary cycles.