| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 4: Completing a Commissioning Log (Case Study Simulation)

Scenario data (steady‑state)

Ambient: 18°C | Room: 26°C | Set point: 21°C | Mode: Cooling

Suction pressure: 6.0 bar(g) | Tsat suction: 6°C (from PT)

Discharge pressure: 19 bar(g) | Tsat discharge: 42°C (from PT)

Suction line temperature: 20°C | Liquid line temperature: 41°C

Indoor air on/off: 26°C → 20°C | Outdoor air on/off: 18°C → 30°C

Running current: Higher than expected at this load (no value given)

A) Complete the commissioning log

Commissioning log template (fill in)

| Field | Value | Field | Value |
| --- | --- | --- | --- |
| Ambient (°C) |  | Room temp (°C) |  |
| Set point (°C) |  | Mode |  |
| Suction pressure |  | Discharge pressure |  |
| Tsat @ suction (°C) |  | Tsat @ discharge (°C) |  |
| Suction line temp (°C) |  | Liquid line temp (°C) |  |
| Superheat (K) |  | Subcooling (K) |  |
| Indoor air on/off |  | Outdoor air on/off |  |
| Running current (A) | ________ (tutor demo) | Voltage (V) | ________ |
| Steady‑state confirmed? | Y / N | Notes |  |

B) Analysis & decision-making

1. Calculate superheat and subcooling for this scenario (show your working).

2. Which TWO additional pieces of information would you want before making any adjustments?

3. List THREE checks you would do before adjusting refrigerant charge.

4. Write one sentence explaining how you would document an adjustment (before/after evidence).