| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 3: Pressure Calculations (Static & Dynamic)

1. Manometer reading

A U-tube manometer shows 25 mmH₂O. Convert this to Pascals (Pa) using P = ρ g h.

2. Dynamic and total pressure

Air flows at 7.0 m/s in a duct where static pressure = 120 Pa. Find dynamic pressure q = ½ ρ v² and the total pressure.

3. Velocity from flowrate

Volume flow = 0.80 m³/s in a 600 mm × 400 mm duct. Calculate air velocity and dynamic pressure.

4. Water system elevation

What pressure (kPa) is required to raise water by 12 m? Use P = ρ g h. Ignore losses.

Extension

1) A Pitot tube reads total pressure 310 Pa; nearby static pressure is 160 Pa. Find dynamic pressure and air velocity (ρ=1.2 kg/m³).

2) A straight 18 m duct has a uniform friction loss of 90 Pa.

(i) What is the friction rate (Pa/m)?

(ii) If velocity increases by 20%, estimate the new dynamic pressure (assume ρ unchanged).

3) A system has a filter (45 Pa), coil (65 Pa) and duct friction (90 Pa). What is the required external static pressure (Pa) at the fan?