| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 1: Fluid Flow & Piping Effects

Instructions: Show all working. Use SI units. Round answers to 2–3 significant figures unless specified.

Questions

Q1. Continuity: m=0.095 kg/s in 7/8" OD (D≈22.2 mm), ρ=12. Find velocity.

Show all working and give answers with correct units.

Given:

A = πD²/4

Q2. Equivalent length: 18 m + two 90° elbows (1.5 m each) + sight glass (0.5 m).

Show all working and give answers with correct units.

Q3. Pressure drop: 45 Pa/m × L_eq. Give kPa.

Show all working and give answers with correct units.

Q4. Oil return check: 3/4" OD riser (D≈19.05 mm), ρ=10, m=0.08 kg/s. Velocity? ≥8 m/s?

Show all working and give answers with correct units.

Q5. Flash gas quality: h_in=250; h_f=200; h_fg=180. x=(h_in−h_f)/h_fg.

Show all working and give answers with correct units.