| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 1: Electrical & Filtration Calculations

Instructions: Show all working. Use SI units. Round answers to 2–3 significant figures unless specified.

Questions

Q1. Single‑phase: 8.5 A at 230 V, PF 0.92. Real power?

Show all working and give answers with correct units.

Given:

P=V·I·PF

Q2. Three‑phase: 400 V (LL), 18 A, PF 0.86. Real power?

Show all working and give answers with correct units.

Given:

P=√3·V_L·I_L·PF

Q3. Energy cost: 6.8 kW × 10 h/day × 22 days; £0.23/kWh. Monthly cost?

Show all working and give answers with correct units.

Q4. PF correction: 12 kW at PF 0.78 → PF 0.95. Find kVAr to add.

Show all working and give answers with correct units.

Given:

S=P/PF; Q=√(S²−P²)

Q5. Filters series ΔP: 45+120+250+60 Pa; fan 700 Pa. Remaining for duct?

Show all working and give answers with correct units.

Q6. CO₂e: 5.2 kg HFC (GWP=2088); 12% leak/yr. Annual CO₂e (tonnes)?

Show all working and give answers with correct units.

Given:

CO₂e(kg)=leak(kg)×GWP