| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 6: Room Heat Load Calculation

Figure 1. Example room used in this exercise.

Assume: South-facing window 3.0 m × 1.5 m (U=1.6 W/m²·K, SHGC=0.6); Walls U=0.35; Roof U=0.20; Floor U=0.25. External 32 °C, Internal 24 °C. 6 occupants (75 W sensible, 55 W latent each). Ventilation 8 L/s per person. Equipment 1.2 kW. Infiltration 0.5 ACH. Use ρ_air=1.2 kg/m³, c_p(air)=1.005 kJ/kg·K.

Tasks

1) Compute fabric gains (W): walls (minus window), window conduction, roof, floor.

2) Compute solar gain through the window using irradiance 500 W/m² and SHGC 0.6.

3) Add internal sensible gains: occupants + equipment.

4) Ventilation sensible load from 8 L/s per person (use ΔT = 8 K).

5) Infiltration sensible load at 0.5 ACH (use room volume).

6) Sum sensible and latent loads; give total cooling load (kW).

7) If supply air is 10 K cooler than room, estimate supply airflow (m³/s).

8) Choose an AC unit: 5.0 kW, 7.1 kW, or 10.0 kW, based on your total.

Extension:

1) Re‑evaluate the sensible load if external rises to 35 °C (ΔT=11 K) and shading halves SHGC to 0.3. Compare to baseline.

2) If only 4 occupants are present and ventilation is 10 L/s per person, recompute the internal sensible and ventilation sensible loads and the new total sensible.

3) With a maximum supply airflow of 0.70 m³/s, what supply ΔT is needed to handle the baseline sensible load?