## Slide 1
Occupational Specialism: Air Conditioning Engineering
K1.3 Scientific principles of air conditioning
PowerPoint 1.3f: Heat transfer

## Slide 2
Objectives
By the end of this session, you should be able to:
Understand and apply the principles of heat transfer.
Understand the concept of temperature and use temperature scales.
Convert values between temperature scales.
Calculate rate of heat transfer.
Understand and calculate a range of variables.

## Slide 3
      Starter: What do you already know?
Work in small groups and answer the question:
How does heat transfer in an air conditioning system allow it to cool a room, even though it doesn’t actually create cold air?
Describe the action of the three main types of heat transfer involved.
Notes: An air conditioner cools a room through heat transfer, not by making ‘cold’. It works by moving heat from inside the room to the outside. Three main types of heat transfer:
1. Conduction: Heat passes through the metal evaporator and condenser coils.
Indoor coil absorbs heat from warm room air.
Outdoor coil releases heat to the outside air.
2. Convection: Fans blow air across the coils to help move heat.
Indoor fan pulls warm room air over the cold evaporator.
Outdoor fan pushes air over the hot condenser coil.
3. Phase Change (latent heat): This is the most important part. The refrigerant evaporates indoors, absorbing heat.
It then condenses outdoors, releasing heat.
Key idea: Air conditioners don’t make cold – they remove heat. Cooling happens because heat is transferred away from the room and dumped outside.

## Slide 4
      Principles of heat transfer
Conduction: heat through solids.
Convection: heat via moving fluids.
Radiation: heat transfer via waves.
AC uses conduction + convection in coils.

## Slide 5
      Heat transfer in systems
Conduction through walls (building materials).
Convection across coils (air across coils).
Radiation from the sun (solar load).
Example
A condenser with blocked fins experiences reduced convection, leading to higher head pressure and increased energy consumption.

## Slide 6
      Temperature
What is temperature?
Temperature is a measure of how hot or cold something is.
Scientifically, it tells us how fast the particles (atoms or molecules) in a substance are moving:
faster particle motion → higher temperature
slower particle motion → lower temperature.
So, temperature reflects thermal energy.

## Slide 7
      Why is temperature important?
1. It determines comfort levels
Air conditioning exists to keep indoor spaces comfortable.
If the temperature is too high or too low, people will feel uncomfortable, regardless of humidity or airflow.
Ideal indoor comfort is usually around 20–24°C.
AC systems constantly monitor temperature to maintain this range.

## Slide 8
      Why is temperature important?
2. It affects how the AC System works
The temperature of indoor and outdoor air impacts how hard the AC must work.
Higher outdoor temperatures → condenser works harder.
Lower indoor temperatures → evaporator removes heat more quickly.
Monitoring temperature helps prevent:
overloading the compressor
ice forming on the evaporator coil
reduced efficiency.

## Slide 9
      Why is temperature important?
3. It ensures energy efficiency
Correct temperature settings reduce energy usage.
Setting an AC too low wastes energy.
Keeping the indoor temperature slightly higher reduces compressor workload.
Good temperature control → lower electricity bills.

## Slide 10
      Why is temperature important?
4. It protects the AC components
Different parts of an AC – compressor coils, refrigerant – must stay within certain temperature ranges.
If temperatures get too high or too low:
refrigerant may not evaporate or condense properly
coils may freeze
the compressor may overheat.
Maintaining proper temperature protects the system from damage.

## Slide 11
      Why is temperature important?
5. It helps control humidity
Temperature and humidity are linked in AC systems.
When warm air is cooled, moisture condenses.
If temperature is not controlled, humidity won’t be controlled either.
Correct temperature = better humidity removal.

## Slide 12
      Why is temperature important?
6. It impacts air quality
Stable temperatures help prevent:
mould growth
excess condensation
poor ventilation.
These factors directly affect indoor air quality.

## Slide 13
      Why is temperature important?
Common temperature-related AC faults
Temperature issues in AC systems often come from:
evaporator freezing
high condenser temperature
incorrect δt across coil
superheat/subcooling issues
thermostat reading errors
airflow restrictions
refrigerant charging problems.

## Slide 14
      Temperature scales
1. Celsius (°C)
Most countries use Celsius. Based on water:
0°C → Water freezes
100°C → Water boils
Invented by Anders Celsius (1742)
Example:
Room temp ≈ 20–25°C
Human body temp ≈ 37°C

## Slide 15
      Temperature scales
1. Celsius (°C)
Most countries use Celsius. Based on water:
0°C → Water freezes
100°C → Water boils
Invented by Anders Celsius (1742)
Example:
Room temp ≈ 20–25°C
Human body temp ≈ 37°C

## Slide 16
      Temperature scales
2. Kelvin (K)
The standard scientific temperature scale.
0 K = absolute zero (lowest possible temperature) → particles have minimum energy
No degree symbol: write K, not °K
Example:
Water freezes at 273 K
Water boils at 373 K

## Slide 17
      Converting between temperature scales
Celsius ↔ Kelvin
K = C + 273
C = K − 273

## Slide 18
      Temperature scales
Summary
Scale | Freezing Point of Water | Boiling Point of Water | Used by
Celsius (°C) | 0°C | 100°C | Most of world
Fahrenheit (°F) | 32°F | 212°F | USA
Kelvin (K) | 273 K | 373 K | Science, engineering

## Slide 19
      Rate of heat transfer
The rate of heat transfer tells you how much heat energy is moved per second.
It is usually measured in:
Watts (W) → joules per second
kW (common in HVAC)
The formula you use depends on the type of heat transfer.

## Slide 20
      Rate of heat transfer
1. Sensible heat transfer (temperature change only)
Used when the temperature is changing without a change of state.
Formula Q˙= m⋅c⋅ΔT
Where:
Q˙​ = rate of heat transfer (W)
m = mass flow rate (kg/s)
c = specific heat capacity (J/kg·°C)
ΔT = temperature difference (°C or K)
Used in AC for:
heating/cooling air • temperature change across coils (evaporator/condenser)

## Slide 21
      Rate of heat transfer
2. Sensible heat transfer for air (HVAC shortcut formula)
HVAC engineers often use a simplified rule because air properties are known.
Metric units Q˙=1.2⋅V˙⋅ΔT
Where:
1.2 = air density × specific heat (kJ/m³·°C)
V˙ = airflow rate (m³/s)
ΔT\ = temperature difference (°C)

## Slide 22
      Rate of heat transfer
3. Latent heat transfer (humidity change)
Used when moisture is added or removed (evaporation/condensation).
Formula Q˙=m⋅L
Where:
L = latent heat of vaporisation (≈ 2,500,000 J/kg for water)
Used in AC for:
dehumidification on the evaporator coil
moisture condensation

## Slide 23
      Rate of heat transfer
4. Conduction heat transfer (heat flowing through walls, pipes, insulation, etc.)
Formula (Fourier’s Law) Q˙= k⋅A⋅ΔT
d
Where:
k = thermal conductivity (W/m·K)
A = area (m²)
d = thickness of the material (m)

## Slide 24
      Rate of heat transfer
Summary
Type of Heat | When Used? | Formula
Sensible | Temperature changes | 
Latent | Humidity changes (moisture removal) | 
Conduction | Heat flow through solids | 
Type of Heat | When Used? | Formula
Sensible | Temperature changes | 
Latent | Humidity changes (moisture removal) | 
Conduction | Heat flow through solids | 
Air (HVAC shortcut) | Cooling/heating air with known airflow | 
Air (HVAC shortcut) | Cooling/heating air with known airflow | 

## Slide 25
      Application of heat calculations
Used for selecting equipment and understanding heat gains, such as using to size coils & evaluate load.
Example
A small classroom with 30 students may have approximately 3–4 kW of sensible heat gain just from occupants.
Add lighting and solar gain to properly size the AC.

## Slide 26
Suggested answer – Use typical classroom values:
Lighting heat gain
Most classrooms have 500–1,000 W of lighting load.
Let’s estimate: 0.5–1.0 kW
Solar gain through windows
Typical solar gain for a small classroom: 1–2
Total approximate heat gain – Adding these components:
Minimum estimate 3 kW (people)+0.5 kW (lights)+1 kW (solar) = 4.5 kW
Higher estimate 4 kW (people)+1 kW (lights)+2 kW (solar) = 7 kW
Answer: Use an AC unit around 6–8 kW (≈ 20,000–27,000 BTU/h)

## Slide 27
      Example – air conditioning
Air enters an evaporator at 26°C and leaves at 16°C. Airflow is 0.5 m³/s.
Step 1: Calculate ΔT
ΔT= 26 − 16 = 10°C
Step 2: Apply the HVAC sensible heat formula
Q˙=1.2⋅0.5⋅10
Q˙=6 kW
Answer: Cooling rate = 6 kW

## Slide 28
      Range of variables
The three major variables in air conditioning are:
cooling capacity
heating capacity
condensate production rate.
Each can be calculated using standard formulas.

## Slide 29
      Range of variables
1. Cooling capacity
Cooling capacity is the amount of heat removed from indoor air per second.
Measured in units:
kW (kilowatts)
BTU/h (British Thermal Units per hour)
kJ/s
Formula (Sensible cooling)
For cooling air without removing moisture: Q˙s = 1.2⋅V˙⋅ΔT
Where:
1.2 = combined constant for air density × specific heat
V˙ = airflow (m³/s)
ΔT=Tin−Tout​

## Slide 30
      Range of variables
Example:
Airflow: 0.5 m³/s
ΔT: 10°C
Q˙s = 1.2⋅V˙⋅ΔT
Q˙=1.2⋅0.5⋅10 = 6 kW

## Slide 31
      Range of variables
2. Heating Capacity
Heating capacity is the amount of heat added to the air.
Measured in units
kW
BTU/h
Formula Q˙h=1.2⋅V˙⋅ΔT
Exactly the same as sensible cooling, but temperature rises instead of falls.
Example:
Airflow: 0.4 m³/s
Temperature rise: 15°C Q˙h=1.2⋅0.4⋅15=7.2 kW

## Slide 32
      Range of variables
3. Quantity of condensate over time
Condensate forms when the evaporator coil removes moisture from warm, humid air.
Why does condensate form?
When air cools below its dew point, water vapour condenses into liquid water.
Relationship to latent heat
Every kg of water condensed removes approximately: L = 2,500,000 J
This links dehumidification to the cooling load:
Q˙h=1.2⋅0.4⋅15=7.2 kW

## Slide 33
      Range of variables
Formula for condensate flow rate
If the latent cooling load is known:
m˙water= Q˙latent
L
​​Where:
m˙water​ = kg/s of condensate
Q˙latent​ = latent cooling (W or J/s)
L = 2.5 × 10⁶ J/kg
Convert to litres/hour
Water density ≈ 1 kg/L Therefore: L/h=m˙water×3600

## Slide 34
      Range of variables
Example: Condensate calculation
Latent cooling load = 5 kW (5000 W)
m˙water = 5000 = 0.002 kg/s
2,500,000
Convert to L/h:
0.002×3600 = 7.2 L/h
This is a typical value for a busy classroom or office AC system.

## Slide 35
      Range of variables
Summary

## Slide 36: Summary
You should now be able to:
Understand and apply the principles of heat transfer.
Understand the concept of temperature and use temperature scales.
Convert values between temperature scales.
Calculate rate of heat transfer.
Understand and calculate a range of variables.

## Slide 37
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.