## Slide 1
Occupational Specialism: Air Conditioning Engineering
K1.3 Scientific principles of air conditioning
PowerPoint 1.3g: Refrigerant fluids and lubricants

## Slide 2
Objectives
By the end of this session, you should be able to:
Understand and apply the principles of refrigerants and lubricants.
Understand and use primary and secondary refrigerants.
Explain their environmental impact.

## Slide 3
      Starter: What do you already know?
As a group, discuss:
Why does an air conditioning system need both refrigerants and lubricants, and what does each one do in the cooling process?
Identify the main role of each.
Notes: Key idea: Refrigerants move heat. Lubricants protect the compressor. Both are essential for safe, efficient, long‑lasting air conditioning operation.
Refrigerants are the working fluid of the system. They absorb heat inside the building and release heat outside by changing between liquid and gas.
Their main jobs:
Absorb heat in the evaporator
Carry heat through the system
Release heat in the condenser
Allow cooling through phase change (evaporation/condensation)
Without refrigerant → no heat transfer → no cooling.
Lubricants are used mainly in the compressor, the system’s hardest‑working component.
Their main jobs:
Reduce friction between moving parts
Prevent wear and overheating
Seal and protect internal surfaces
Help remove heat from the compressor
Without proper lubrication → compressor damage, overheating, and system failure.

## Slide 4
      Refrigerants and Lubricants
Refrigerants change state easily (liquid ↔ gas).
Lubricants must tolerate chemical + temperature stresses.
Common types:
hydrofluorocarbons (HFC)
hydrofluoroolefins (HFO)
hydrocarbon (HC) natural refrigerants.

## Slide 5
      Properties of refrigerants
Refrigerants are the working fluids that absorb and release heat as they circulate through an air‑conditioning system.
Key properties include:
1. Thermodynamic properties
Boiling point | Should be low at atmospheric pressure so the refrigerant can evaporate at low temperatures
Latent heat of vaporisation | High latent heat allows more cooling per kilogram of refrigerant
Operating pressures | Should be compatible with system components, safe, and efficient
Critical temperature and pressure . | Higher critical temperature improves efficiency in warmer climates

## Slide 6
      Properties of refrigerants
2. Chemical properties
Stability | Must remain stable and not decompose under normal temperatures and pressures inside the system
Non‑corrosive | Should not corrode metals or degrade plastics and elastomers used in piping and seals
Compatibility with lubricants | The refrigerant must mix appropriately with the compressor oil to ensure proper lubrication

## Slide 7
      Properties of refrigerants
3. Safety properties
Toxicity | Modern refrigerants aim to be low-toxicity to protect building occupants and service technicians
Flammability | Some newer low‑GWP refrigerants (e.g. R‑32) are mildly flammable and classified under ASHRAE safety groups

## Slide 8
      Properties of refrigerants
4. Environmental properties
Ozone Depletion Potential (ODP) | Should be zero – e.g. R‑410A, R‑32, R‑134a
Global Warming Potential (GWP) | Increasingly important – newer refrigerants aim for low GWP (e.g. R‑32, R‑1234yf)

## Slide 9
      Properties of lubricants
Lubricants ensure the compressor operates smoothly and reliably. Their properties must match the refrigerant and compressor type.
1. Viscosity
Must maintain enough thickness (film strength) to lubricate moving parts.
Must not become too thick in cold conditions or too thin in hot conditions.

## Slide 10
      Properties of lubricants
2. Chemical stability
Should resist oxidation and breakdown during high‑temperature compressor operation.
Must not react with refrigerant or system materials.
3. Miscibility with refrigerants
Fully miscible oils (e.g. POE with R‑410A) help return oil to the compressor.
Non‑miscible oils may require special design considerations.

## Slide 11
      Properties of lubricants
4. Moisture control
Oils must have low hygroscopicity (absorption of water), although POE oils are highly hygroscopic and require careful handling.
Moisture causes acid formation and system corrosion.
5 Dielectric strength
Important in hermetic compressors where oil surrounds electrical windings.
Oil must act as an electrical insulator.

## Slide 12
      Properties of lubricants
Lubricant types used in air conditioning
Mineral Oil (MO)
Used with older CFC/HCFC refrigerants like R‑22.
Polyolester (POE)
Used with modern HFC refrigerants like R‑410A, R‑134a.
Polyalkylene Glycol (PAG)
Mainly used in automotive AC systems.
Alkylbenzene (AB)
Highly stable, used in some older systems.

## Slide 13
      Properties of lubricants
Compatibility between refrigerants and lubricants
Matching refrigerant and lubricant is essential for:
proper oil return
compressor cooling
seal protection
preventing chemical reactions.
Examples:
R‑410A → POE oil
R‑32 → POE oil
R‑134a → POE oil
R‑22 → Mineral oil (MO) or AB oil

## Slide 14
      Primary refrigerants – Hydrofluorocarbons (HFCs)
HFC refrigerants were introduced as replacements for ozone‑depleting CFCs and HCFCs.
Key characteristics:
No ozone depletion potential (odp = 0) – they do not damage the ozone layer.
High Global Warming Potential (GWP) – this is their main environmental drawback.
Examples:
R‑134a → GWP ≈ 1430
R‑410A → GWP ≈ 2088
Chemically stable and non‑flammable
Most HFCs fall under ASHRAE safety group A1.

## Slide 15
      Primary refrigerants – Hydrofluorocarbons (HFCs)
Common HFCs used in air conditioning:
R‑134a – used in commercial refrigeration and automotive AC (older vehicles).
R‑410A – widely used in domestic and commercial split AC.
R‑407C – used in some heat pumps and AC systems.

## Slide 16
      Primary refrigerants – Hydrofluorocarbons (HFCs)
HFOs are the latest generation of synthetic refrigerants, designed to have a low climate impact.
Key characteristics:
Very low GWP (often below 1)
For example: R‑1234yf → GWP < 1
Zero Ozone Depletion Potential (ODP = 0)
Mildly flammable
Classified as A2L under ASHRAE.
Good energy efficiency
Often comparable to or better than HFCs.

## Slide 17
      Primary refrigerants – Hydrofluoroolefins (HFOs)
Common HFO refrigerants used in air conditioning:
R‑1234yf – modern automotive air conditioning.
R‑1234ze – chillers and industrial cooling.
R‑454B – replacement for R‑410A in split AC.

## Slide 18
      Primary refrigerants – Hydrocarbon (HC)
Hydrocarbons are naturally occurring refrigerants.
They offer excellent thermodynamic performance and very low climate impact.
Key characteristics:
Very low GWP
Example values: Propane (R‑290) → GWP ≈ 3
Isobutane (R‑600a) → GWP ≈ 3
Zero Ozone Depletion
High efficiency
Often higher than synthetic refrigerants.
Flammable – classified A3 (highly flammable).

## Slide 19
      Primary refrigerants – Hydrocarbon (HC)
Common HC refrigerants in air conditioning:
R‑290 (Propane) – heat pumps, split AC, commercial refrigeration.
R‑600a (Isobutane) – domestic refrigerators.
R‑1270 (Propylene) – industrial systems.

## Slide 20
      Primary refrigerant – ideal properties
Although each refrigerant family has different characteristics, the ideal refrigerant – regardless of type – should meet specific:
thermodynamic
safety
chemical
environmental criteria.

## Slide 21
      Primary refrigerant – ideal properties
1. Thermodynamic properties
Low boiling point – allows efficient evaporation at low temperatures.
High latent heat of vaporisation – increases cooling capacity per kilogram of refrigerant.
Moderate operating pressures – pressures should be:
high enough to avoid air infiltration
low enough for safe, cost‑effective system components.
High critical temperature – ensures the refrigerant remains efficient in hot climates.
Good heat transfer characteristics – high thermal conductivity to improve system performance.

## Slide 22
      Primary refrigerant – ideal properties
2. Chemical properties
Chemically stable – no decomposition at operating temperatures/ pressures.
Non‑corrosive – safe for metals, plastics, elastomers, oils, and motor windings.
Compatible with lubricants – must mix or return oil to the compressor effectively.
Non‑reactive with moisture – ideally should not form acids or sludge.

## Slide 23
      Primary refrigerant – ideal properties
3. Safety properties
Low toxicity – safe for service technicians and building occupants.
Low flammability – ideally non‑flammable (A1), but some modern low‑GWP refrigerants are mildly or fully flammable.
Detectable leak – should have characteristics that allow easy leak detection.

## Slide 24
      Primary refrigerant – ideal properties
4. Environmental properties
Zero Ozone Depletion Potential (ODP = 0) – must not harm the ozone layer.
Low Global Warming Potential (GWP) – preferably very low or ultra‑low, in line with global F‑Gas reductions.
Short atmospheric lifetime – breaks down quickly, reducing long‑term climate impact.

## Slide 25
      Primary refrigerant – ideal properties
Summary
Property Type | Ideal Characteristics
Thermodynamic | Low boiling point, high latent heat, high critical temp, moderate pressure
Chemical | Stable, non‑corrosive, oil‑compatible, non‑reactive with moisture
Safety | Non‑toxic, non‑flammable, easy leak detection
Environmental | ODP = 0, very low GWP, short atmospheric lifetime

## Slide 26
      Ideal properties – Hydrofluorocarbons (HFCs)
Zero ODP
Moderate GWP (traditional HFCs have high GWP, but the ideal HFC would be lower)
Non‑flammable (A1 safety rating)
Chemically stable
Compatible with POE oils
Good thermodynamic efficiency
Note: Actual HFCs have high GWP, which is their major drawback.
Used widely in air‑conditioning and refrigeration, but is being phased out.

## Slide 27
      Ideal properties – Hydrofluoroolefins (HFOs)
Ultra‑low GWP (<1 whenever possible)
Zero ODP
Good energy efficiency
Chemically stable but decomposes quickly in atmosphere
Low toxicity
Mild flammability (A2L)—ideally as low as possible
Note: Mild flammability is currently unavoidable due to their molecular structure.
New generation refrigerants designed for minimal environmental impact.

## Slide 28
      Ideal properties – Hydrocarbon (HC)
Very low GWP (typically 3 or below)
Zero ODP
Excellent thermodynamic efficiency
Good compatibility with oils and materials
Widely available and inexpensive
Note: Their main drawback is high flammability (A3). Charge‑size limits apply in many applications.
Used in heat pumps, fridges, and increasingly in split AC.

## Slide 29
      Secondary refrigerants
Secondary refrigerants – also called secondary coolants or chilled fluids – are liquids used to transport cooling from a central refrigeration plant to various spaces or processes.
Unlike primary refrigerants, they do not undergo phase change in normal operation.
Instead, they absorb heat as they circulate through a system.

## Slide 30
      Secondary refrigerants
A secondary refrigerant is a fluid that is cooled by the primary refrigeration system. It then circulates through the building or equipment and absorbs heat before returning to be cooled again.
They help reduce:
the amount of primary refrigerant needed
the risk of leaks
installation cost and complexity in large buildings.

## Slide 31
      Common secondary refrigerants
Chilled water
The most common secondary refrigerant in air conditioning systems.
Water–glycol solutions
Used where freezing protection is required.
Brines
Used mainly in industrial or low‑temperature cooling.
Special low‑freezing fluids
Used in specialised AC or refrigeration systems.

## Slide 32
      Secondary refrigerants – ideal properties
Thermal properties
High specific heat (absorbs lots of heat)
Good thermal conductivity
Low freezing point (especially for glycol or brines)
Low viscosity (easy to pump)
Chemical properties
Stable at operating temperatures
Non‑corrosive to system materials
Compatible with seals, metals, and plastics

## Slide 33
      Secondary refrigerants – ideal properties
Safety and Environmental properties
Non‑toxic
Non‑flammable
Low environmental impact
Easy to handle and store
Economic properties
Low cost
Readily available
Long service life

## Slide 34
      Use of secondary refrigerants
Secondary refrigerants are widely used in:
large commercial air‑conditioning (chilled‑water systems)
district cooling plants
data centres and server cooling systems
air handling units (AHUs)/fan coil units (FCUs)
process cooling in industry.

## Slide 35
      Environmental impacts
Summary

## Slide 36
      Global Warming Potential (GWP) and Ozone Depletion Potential (ODP) comparison
Refrigerant | Type | ODP | GWP (100‑yr)
R‑12 | CFC | 1.0 | 10,900
R‑22 | HCFC | 0.05 | 1,810
R‑32 | HFC | 0 | 675
R‑125 | HFC | 0 | 3,500
R‑134a | HFC | 0 | 1,430
R‑143a | HFC | 0 | 4,300
R‑404A | Blend (HFC) | 0 | 3,922
R‑407C | Blend (HFC) | 0 | 1,774
R‑410A | Blend (HFC) | 0 | 2,088 (EPA/industry standard value)
R‑454B | HFO blend | 0 | 466
R‑1234yf | HFO | 0 | 4
R‑1234ze | HFO | 0 | 6
R‑290 (Propane) | Natural | 0 | 3
R‑600a (Isobutane) | Natural | 0 | 3
R‑717 (Ammonia) | Natural | 0 | 0
R‑744 (CO₂) | Natural | 0 | 1
Environmental Rating
🟥 Very high impact
🟥 High GWP / low ODP
🟧 Medium GWP
🟥 High GWP
🟧 Medium‑high GWP
🟥 Very high GWP
🟥 Very high GWP
🟧 Medium‑high GWP
🟥 High GWP
🟩 Low GWP
🟩 Ultra‑low GWP
🟩 Ultra‑low GWP
🟦 Natural refrigerant (very low GWP)
🟦 Natural refrigerant (very low GWP)
🟦 Natural refrigerant (zero GWP)
🟦 Natural refrigerant (reference baseline GWP 1)

## Slide 37
      Lubricants – ideal properties
Lubricants (compressor oils) must protect the compressor, ensure efficient operation, and remain stable throughout the system.
The ideal lubricant should have the following properties:
1. Viscosity
Correct viscosity at both high and low temperatures
High viscosity index
Good film strength

## Slide 38
      Lubricants – ideal properties
2. Chemical stability
Resists oxidation and thermal breakdown
Stable in the presence of refrigerant
Low moisture absorption
3. Compatibility
Compatible with system materials
Compatible with the refrigerant
Does not cause swelling or deterioration of elastomers

## Slide 39
      Lubricants – ideal properties
4. Lubrication performance
High lubricity
Low foaming tendency
Good demulsibility
5. Electrical properties
High dielectric strength
Non‑conductive
6. Thermal properties
Good heat‑carrying ability
Low pour point

## Slide 40
      Lubricants – ideal properties
7. Environmental and safety properties
Low toxicity
Low environmental impact
Biodegradability (where applicable)
8. Economic properties
Reasonable cost
Long service life
Easily available and handled safely

## Slide 41: Summary
You should now be able to:
Understand and apply the principles of refrigerants and lubricants.
Understand and use primary and secondary refrigerants.
Explain their environmental impact.

## Slide 42
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.