| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 3: Troubleshooting & Diagnostics

K1.1 The function and operation of air conditioning systems

- A fan coil unit is not providing cooling.
List at least five possible causes and outline diagnostic steps.

- A VRF indoor unit shows fluctuating supply-air temperatures.

  - Identify likely system issues.

  - Explain what measurements they would take (e.g., refrigerant pressures, thermistor readings).

- An AHU coil is frosting.
Identify potential root causes and propose corrective actions.

Answers

- FCU not cooling – possible causes:

- Blocked filter

- Closed or faulty chilled-water valve

- Air trapped in coil

- Chilled-water pump failure

- Low refrigerant (DX FCU)

- Dirty coil

- Faulty thermostat

- Controls/sensors: Faulty/incorrectly located thermostat, sensor out of calibration, BMS schedule/override, setpoint too high, flat batteries (if local stat).

- Condensate safety/float switch trip: Pan full due to blocked drain

- Electrical: Tripped MCB, loose connections, failed contactor/relay

Diagnostic sequence (logical, safe steps)

- Visual & basic checks: Power available, fan running, filters clean, coil condition, condensate tray and drain clear.

- Airflow verification: Measure supply airflow vs. design; check external static pressure; inspect fan wheel and belts.

- Water side (if CHW): Confirm supply/return water temps (e.g., 6–8 °C supply, 12–14 °C return typical), valve actuation, coil DP, vent air from coil; verify pump status and differential pressure.

- DX side (if applicable): Check suction/discharge pressures, superheat/subcooling, EEV actuation/steps, frost on evaporator.

- Controls: Verify setpoint, occupancy/schedule, mode (cooling), sensor readings vs. actual, BMS interlocks, any lockouts/alarms.

- Outcome test: After each corrective action, recheck supply‑air temperature drop (ΔT ≈ 8–12 K typical depending on design).

2. VRF temperature fluctuation issues:

- Incorrect refrigerant charge

- Faulty sensors and controls e.g. thermistors

- Branch selector malfunction

- Obstructed or dirty indoor coil

- Poor load diversity or control settings

- Intermittent defrost in heating mode causing temperature swings

Measurements learners should take:

- Temperatures: Room, return, supply, indoor coil in/out; outdoor ambient; refrigerant line temps (liquid/suction).

- Pressures: Suction/discharge pressures at service ports; calculate superheat and subcooling.

- Electrical/inverter: Compressor frequency (Hz), inverter current, outdoor fan speed.

- EEV data: Step position/command vs. actual (if service tool available).

- Branch selector (heat recovery): Port temperatures, mode status, cross‑leak checks.

- Airflow: Indoor unit airflow (anemometer/flow hood) vs. nameplate; filter ΔP.

- Thermistors: Resistance vs. temperature chart (compare to manufacturer table); check for drift.

- Controls/BMS: Mode conflicts, setpoints, deadbands, schedules, error history.

3. AHU coil frosting causes:

- Low airflow (blocked filters, belt issues)

- Low chilled-water temperature

- Faulty control valve

- Incorrect refrigerant valve operation (in DX AHUs)

- High latent load / low mixed‑air temperature

Corrective actions

- Restore airflow: Replace filters, clean coil, verify fan curve/VFD speed, correct damper positions, fix belt tension.

- Control the coil temperature:

- CHW: Implement/reset SAT or CHW reset strategy; verify valve control/actuator; limit minimum CHW supply (e.g., not below ~5–6 °C unless designed).

- DX: Check charge, correct EEV superheat target, confirm defrost/frost protection logic.

- Manage outdoor air & humidity: Ensure economiser logic correct; reduce OA to design minimum when cold/humid; consider preheat coil or reheat/dehumidification if required.

- Enable frost protection: Install/validate frost coil sensor; add low‑limit cutout; implement staged unloading or min fan cfm limits.