| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 4: Refurbishing an HVAC system

K1.1 The function and operation of air conditioning systems

- Scenario

You are tasked with refurbishing the HVAC system in a medium size office building.

Choose between VRF, DX, or a chilled water system.

Justify your selection based on:

  - Building layout

  - Energy efficiency

  - Maintenance

  - Installation complexity

  - Zoning needs

2. Given performance data, determine which type of heat pump (air, ground, or water source) is most suitable for a school building and explain the reasoning.

Tutor guidance

Provide some performance data for Question 2 for learners to use.

- Office refurbishment recommendation:

- VRF: Best for zoning, retrofit ease, efficiency.

- Chilled water: Suitable only if a large building has an existing plant.

- DX: Only for very small office zones.

| Criterion | DX | VRF | Chilled Water |
| --- | --- | --- | --- |
| Building layout | Best for small/simple zones | Excellent for multi-zone floors | Best for large/campus with plant |
| Energy efficiency | Moderate; poorer part-load | Very good at part-load; heat recovery | High with optimised plant & pumps |
| Maintenance | Simple unit servicing | Requires VRF-trained techs | Plant + water treatment; more complex |
| Install complexity | Low, minimal controls | Medium; refrigerant routing & BS boxes | High; risers, pumps, AHUs, valves |
| Zoning needs | Limited | Excellent (indoor unit per zone) | Good with FCUs/VAV but more plant |

Model recommendation (typical outcome)

- For a medium‑size office with multiple rooms and meeting spaces, VRF is usually optimal:

- Pros: Zoning & individual control, high part‑load efficiency, potential heat recovery between sun‑exposed and shaded zones, lower disruption in retrofit than CHW.

- Cons: Specialist maintenance, refrigerant routing/design diligence required.

- If the office is very simple single‑zone → DX split/packaged can be cost‑effective.

- If the building is part of a larger estate or already has plant and future expansion → chilled water may be best long‑term.

2. Heat pump for a school:

- Ground source: Best efficiency for long-term cost savings.

- Air source: Acceptable if budget constrained.

- Water source: Ideal if nearby water bodies are available.

Model method

- Normalize the data: Compare COP/EER at standard rating points and at design ambient (e.g., 7 °C and −2 °C for heating; 35 °C for cooling).

- Account for defrost (ASHP): Deduct defrost penalties or use seasonal COP/SCOP where provided.

- Check site constraints:

  - GSHP: Borehole count/depth, drilling feasibility, ground thermal conductivity.

  - WSHP: Water body/ambient loop availability, permissions.

  - ASHP: Roof/yard space, acoustic limits.

- Cost & lifecycle: Capex, Opex (electricity tariff), maintenance, likely run hours (schools: high day-time, low night/weekend).

- Resilience & noise: School environments benefit from quieter plant (GSHP/WSHP advantage).

Example conclusion pattern

- If data shows GSHP COP 4.5 at 0–5 °C source vs ASHP COP 3.0 at 7 °C & 2.3 at −2 °C, and the site permits boreholes → Recommend GSHP for quieter operation and lower energy over life.

- If boreholes not feasible and climate is mild, with good part-load modulation and low-noise ASHP units → Recommend ASHP.

- If a campus ambient water loop exists (or lake/river with permits) → WSHP could deliver top performance with moderate capex.