| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 2: p–h Chart Cycle Labelling

K1.10 Principles of operation of heat pumps

What you will do

Interpret the axes of a pressure–enthalpy (p–h) chart.

Label the four processes on a heat pump cycle and link each to a component.

Identify where heat is absorbed and rejected and where work is added.

Resources

Your class p–h chart handout or the p–h chart slide in the lesson.

Pen/pencil + highlighter.

Instructions (15–20 minutes)

- Work in pairs.

- Use the p–h chart shown in the lesson and follow the cycle direction 1 → 2 → 3 → 4 → 1.

- Complete the tasks below and write answers clearly.

Tasks

Label the axes: what is on the x-axis? What is on the y-axis?

Mark points 1, 2, 3, 4 on the cycle and write what component sits between each pair:

Identify which process is approximately constant enthalpy (h ≈ constant).

Shade/underline the section where the refrigerant absorbs heat from the source.

Shade/underline the section where the refrigerant delivers heat to the building.

Circle the section that represents compressor work input.

Cycle table (fill in)

| Process | Component | What happens to pressure? | What happens to enthalpy? | Heat/work interaction |
| --- | --- | --- | --- | --- |
| 1 → 2 |  |  |  |  |
| 2 → 3 |  |  |  |  |
| 3 → 4 |  |  |  |  |
| 4 → 1 |  |  |  |  |

Maintenance link (write one each)

For each component, write ONE maintenance check that helps performance (e.g., coil cleanliness, airflow, superheat).

| Component | Maintenance check |
| --- | --- |
| Evaporator |  |
| Compressor |  |
| Condenser |  |
| Expansion device |  |

Tutor guidance

1. Axes:

• X-axis: Enthalpy (h)

• Y-axis: Pressure (p)

2. Cycle Components:

• 1 → 2: Compressor

• 2 → 3: Condenser

• 3 → 4: Expansion device

• 4 → 1: Evaporator

3. Constant Enthalpy Process:

• 3 → 4 (Expansion Valve)

4. Heat Absorption:

• 4 → 1 (Evaporation Process)

5. Heat Rejection:

• 2 → 3 (Condensing process)

6. Compressor Work Input:

• 1 → 2 (compression process)

Cycle Table:

1 → 2 | Compressor | Pressure increases | Enthalpy increases | Work input

2 → 3 | Condenser | Pressure constant / no slight drop | Enthalpy decreases | Heat rejected

3 → 4 | Expansion device | Pressure drops | Enthalpy constant | Throttling (no heat/work)

4 → 1 | Evaporator | Pressure slight rise but low | Enthalpy increases | Heat absorbed

Maintenance Checks:

• Evaporator: Coil cleanliness / airflow check

• Compressor: Check oil level / current draw

• Condenser: Clean coil / airflow

• Expansion device: Verify correct superheat/subcool