| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 3: COP from Enthalpy (Worked Calculations)

Key formulae

Heating COP (COPₕ) = Qout / Win

On a p–h chart (per kg of refrigerant):

Qout ≈ h2 − h3 (condenser heat delivered)

Win ≈ h2 − h1 (compressor work input)

So: COPₕ ≈ (h2 − h3) / (h2 − h1)

Instructions (20–25 minutes)

- Work individually first, then check answers with a partner.

- Show your workings.

- Round COP to 2 decimal places.

Questions

Question 1: Given h1 = 410 kJ/kg, h2 = 460 kJ/kg, h3 = 260 kJ/kg.

a) Calculate Qout (h2 − h3) = __________ kJ/kg

b) Calculate Win (h2 − h1) = __________ kJ/kg

c) Calculate COPₕ = Qout / Win = __________

Question 2: Given h1 = 395 kJ/kg, h2 = 455 kJ/kg, h3 = 275 kJ/kg.

a) Calculate Qout (h2 − h3) = __________ kJ/kg

b) Calculate Win (h2 − h1) = __________ kJ/kg

c) Calculate COPₕ = Qout / Win = __________

Question 3: Given h1 = 420 kJ/kg, h2 = 470 kJ/kg, h3 = 290 kJ/kg.

a) Calculate Qout (h2 − h3) = __________ kJ/kg

b) Calculate Win (h2 − h1) = __________ kJ/kg

c) Calculate COPₕ = Qout / Win = __________

Thinking question (maintenance + performance)

A dirty outdoor coil increases the temperature lift. Explain how this could change h2 − h1 and what happens to COP as a result.

Extension (challenge)

If the compressor power input is 2.5 kW and COPₕ is 3.2, what is the heat output to the building (kW)?

Tutor guidance

Question 1

a) Qout = 460 − 260 = 200 kJ/kg

b) Win = 460 − 410 = 50 kJ/kg

c) COPh = 200 / 50 = 4.00

Question 2

a) Qout = 455 − 275 = 180 kJ/kg

b) Win = 455 − 395 = 60 kJ/kg

c) COPh = 180 / 60 = 3.00

Question 3

a) Qout = 470 − 290 = 180 kJ/kg

b) Win = 470 − 420 = 50 kJ/kg

c) COPh = 180 / 50 = 3.60

Thinking question

A dirty outdoor coil increases temperature lift, meaning the compressor must raise pressure more. This increases h2 − h1 (work input (Win)) and reduces COP.

Extension

Heat output = COPh × compressor power = 3.2 × 2.5 kW = 8.0 kW