| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 5: Maintenance & Fault Symptoms (Diagnosis)

Aim

Identify likely causes of common performance symptoms.

Choose safe first checks a technician would make.

Explain how faults can change pressures/temperatures and reduce COP.

Instructions (15–20 minutes)

Work in pairs.

For each symptom, choose the most likely cause(s).

Write TWO safe first checks you would carry out (e.g., visual inspection, airflow, filter condition, temperature readings).

Do not suggest unsafe actions.

Symptom → Cause → Checks

| Symptom | Most likely cause(s) | Two safe first checks | How COP/cycle might change (brief) |
| --- | --- | --- | --- |
| Low heat output + low suction pressure + high superheat |  |  |  |
| High discharge pressure + poor heat output |  |  |  |
| Outdoor unit icing + frequent defrost |  |  |  |
| High power draw + noisy compressor |  |  |  |
| Short cycling (on/off frequently) + comfort complaints |  |  |  |

Plenary: Explain in your own words

1) Why does reduced airflow across a coil reduce heat pump efficiency?

2) Why is correct flow temperature (emitters/controls) important for COP?

3) One key thing I learned today about p–h charts is: ____________________

Exit ticket (1 minute)

Write one question you still have about heat pumps, COP, or p–h charts:

Tutor guidance

Low heat output + low suction pressure + high superheat:

Cause: Low refrigerant charge or evaporator airflow restriction.

Checks: Visual leak inspection, check filters/airflow.

Cycle impact: Reduced evaporator heat absorption lowers COP.

High discharge pressure + poor heat output:

Cause: Dirty condenser coil or airflow blockage.

Checks: Inspect condenser coil cleanliness, ensure fan operation.

Cycle impact: High condensing pressure increases compressor work, reducing COP.

Outdoor unit icing + frequent defrost:

Cause: Low airflow or low outdoor temperature with humidity.

Checks: Check fan operation, inspect coil for blockage.

Cycle impact: Frequent defrost reduces heating time and COP.

High power draw + noisy compressor:

Cause: Overcharge, mechanical wear, or high head pressure.

Checks: Listen for abnormal noise, check condenser airflow.

Cycle impact: Higher work input reduces COP.

Short cycling + comfort complaints:

Cause: Oversized system or faulty thermostat.

Checks: Check thermostat placement, inspect airflow.

Cycle impact: Inefficient operation lowers seasonal COP.

Plenary

1) Reduced airflow lowers heat transfer, reducing efficiency.

2) Correct flow temperature keeps lift low, improving COP.

3) p–h charts show how pressure and enthalpy change through the cycle.