| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 6: Heat Pump Basics (Starter)

K1.10 Heat pumps | System maintenance

Use Q = m c ΔT, Q = m L, and Power = Q/Δt. Take c_p(water)=4.186 kJ/kg·K, c_p(air)=1.005 kJ/kg·K.

- Sensible cooling

How much energy (kJ) is removed to cool 2.5 kg of water from 30 °C to 5 °C?

- Latent + sensible

How much energy to melt 1.2 kg of ice at 0 °C and then heat the water to 20 °C? (L_f(ice)=334 kJ/kg)

- Energy over time

An AC removes 8.5 kW for 2 hours. How much energy is removed in kWh and kJ?

- Coil sensible load from airflow

Airflow = 0.60 m³/s, ρ=1.2 kg/m³, cool from 28 °C to 16 °C. Find sensible load (kW).

- Refrigerant mass flow

If coil load is 12 kW and refrigerant enthalpy drop is 35 kJ/kg, find mass flow (kg/s).

Extension

1) An AC delivers 7.5 kW of cooling with COP = 3.2 for 3 hours. Find electrical energy (kWh) and cost at £0.28/kWh.

2) Heat 10 kg of glycol (c_p ≈ 3.6 kJ/kg·K) from 10 °C to 65 °C in 25 minutes. Find energy (kJ) and average power (kW).

3) For a 12 kW evaporator, find refrigerant mass flow (kg/s) if Δh is (i) 28 kJ/kg and (ii) 42 kJ/kg. Comment on how Δh affects ṁ.

Tutor guidance

1: Q = m c ΔT = 2.5×4.186×(5-30) = -261.6 kJ (heat removed; magnitude 261.6 kJ)

2: Melt: 1.2×334 = 400.8 kJ; Heat: 1.2×4.186×20 = 100.5 kJ; Total = 501.3 kJ

3: E = 8.5 kW × 2 h = 17.00 kWh = 61200 kJ

4: ṁ = ρQ = 0.72 kg/s; Q = ṁ c ΔT = 8.68 kW

5: ṁ = Q/Δh = 12/35 = 0.343 kg/s

Extension

1) Power in = 2.344 kW; Energy = 7.03 kWh; Cost ≈ £1.97.

2) Q ≈ 1980 kJ; Avg power ≈ 1.32 kW.

3) ṁ: 28 kJ/kg → 0.429 kg/s; 42 kJ/kg → 0.286 kg/s (larger Δh → smaller ṁ).