| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 1: Preparing for Commissioning & Steady‑State Checks

What you will do

Scenario

You are supporting an engineer to commission a newly installed split air‑conditioning system. Before any measurements are taken, you must plan what data to collect, where to measure it, and how to confirm the system is at steady‑state.

A) Pre‑commissioning safety & readiness checklist (tick when complete)

I can describe the main hazards (electric shock, rotating fans, hot surfaces, pressurised refrigerant).

I know what PPE is required for routine commissioning measurements.

I can explain why refrigerant must not be vented and what recovery equipment is for.

I can identify where the indoor and outdoor unit air inlets/outlets are.

I can identify where pressure test points/service ports are (if present) and why caps must be refitted.

B) Plan your measurement locations

On the sketch below, label where you would measure each item. (Use arrows/notes.)

• Ambient temperature  • Room temperature  • Indoor air on/off  • Outdoor air on/off (if required)

• Suction pressure  • Discharge pressure  • Suction line temperature  • Liquid line temperature  • Running current

(Attach your labelled sketch here)

C) Steady‑state & recording conditions

1. Define “steady‑state operation” in your own words.

2. List THREE signs that the system is not yet at steady‑state.

3. Explain why recording data too early could lead to wrong commissioning decisions.

4. What operating conditions must you write down alongside your readings (e.g., mode, set point, fan speed)?

Extension (optional)

In one paragraph, explain how good commissioning improves energy efficiency and comfort.

Tutor guidance

Scenario

You are supporting an engineer to commission a newly installed split air‑conditioning system. You must plan what data to collect, where to measure it, and how to confirm steady‑state.

A) Pre‑commissioning safety & readiness (model)

✓ Hazards: electrical shock; rotating fans; sharp edges; hot discharge pipework; pressurised refrigerant; slips/trips; working at height; manual handling.

✓ PPE: safety footwear; eye protection; task-appropriate gloves; long sleeves; hearing protection if required; site PPE as instructed.

✓ No venting: refrigerant is hazardous and environmentally harmful; recovery equipment prevents release and supports compliance.

✓ Identify indoor/outdoor airflow paths: return/supply at indoor; inlet/discharge at outdoor; avoid recirculation during tests.

✓ Service ports: locate low/high ports if fitted; caps must be refitted as secondary seal and to keep out dirt/moisture.

B) Plan your measurement locations (model)

Instead of a sketch, this teacher copy provides a written model map of measurement points:

Measurement locations

Ambient temperature: shaded position near outdoor unit air inlet (not in direct sun and not in discharge air).

Room temperature: consistent occupant-level location away from supply jet, windows, and heat sources.

Indoor air on/off: return air (air on) and supply air (air off) in free airflow for each indoor unit.

Outdoor air on/off (if required): inlet and discharge positions while avoiding recirculation.

Pressures: suction (low-side) at low service port; discharge (high-side) at high service port (where fitted).

Pipe temperatures: suction line clamp (insulated) near manufacturer-recommended point; liquid line clamp as specified.

Running current: clamp meter on appropriate supply conductor; record at full load and near set point.

C) Steady‑state & recording conditions (model answers)

1. Steady‑state: system has stabilised so key readings change only slightly over time under consistent mode and load.

2. Not steady‑state indicators: rapid pressure swings, compressor/fan ramping, supply air temp drifting quickly, defrost cycle, frequent cycling, room conditions changing (doors/windows).

3. Too-early readings can mislead diagnosis (e.g., incorrect charge conclusion) leading to unnecessary/incorrect adjustments and reduced efficiency.

4. Record alongside readings: mode, set point, fan speed, time since start, ambient, load state (full load/near set point), any special settings, and notable site conditions.

Extension (example)

Good commissioning improves energy efficiency by ensuring correct charge, airflow, and control settings so the compressor does less unnecessary work and avoids short cycling/long run times; it also improves comfort by achieving stable room temperature near set point.