| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 2: Commissioning mini-task (pre-filled)

Purpose

During commissioning you record suction and discharge pressures. To calculate superheat and subcooling, you must convert pressures into saturation temperatures using PT data for the correct refrigerant.

Instructions

Use the PT table/app provided by your tutor for the stated refrigerant. Fill in the missing Tsat values.

Important: use the correct units and state whether the pressure is gauge or absolute if your PT source requires it.

A) PT conversion table (complete Tsat values)

| Case | Refrigerant | Suction pressure | Tsat @ suction (°C) | Discharge pressure | Tsat @ discharge (°C) |
| --- | --- | --- | --- | --- | --- |
| 1 | Tutor-specified | 6.0 bar(g) |  | 19 bar(g) |  |
| 2 | Tutor-specified | 7.2 bar(g) |  | 24 bar(g) |  |
| 3 | Tutor-specified | 5.5 bar(g) |  | 21 bar(g) |  |
| 4 | Tutor-specified | 8.0 bar(g) |  | 26 bar(g) |  |

B) Understanding checks

1. Why must you use the correct refrigerant when converting pressure to Tsat?

2. Give TWO reasons why a pressure reading might be misleading if you do not record operating conditions.

3. Explain the difference between gauge pressure and absolute pressure (one sentence each).

Practical mini-task (in pairs)

Your tutor will demonstrate a pressure probe/manifold. Identify where the low and high-side connections go and explain why service port caps must be refitted after testing.

Tutor guidance

A) PT conversion table (teacher guidance)

Enter Tsat values using the PT table/app that matches the refrigerant used in your lesson. This copy provides “what correct looks like” (process + checks).

PT conversion (pre-filled placeholders)

| Case | Refrigerant | Suction pressure | Tsat @ suction (°C) | Discharge pressure | Tsat @ discharge (°C) |
| --- | --- | --- | --- | --- | --- |
| 1 | [Tutor specifies refrigerant] | 6.0 bar(g) | [Insert Tsat from PT source] | 19 bar(g) | [Insert Tsat from PT source] |
| 2 | [Tutor specifies refrigerant] | 7.2 bar(g) | [Insert Tsat from PT source] | 24 bars(g) | [Insert Tsat from PT source] |
| 3 | [Tutor specifies refrigerant] | 5.5 bar(g) | [Insert Tsat from PT source] | 21 bars(g) | [Insert Tsat from PT source] |
| 4 | [Tutor specifies refrigerant] | 8.0 bar(g) | [Insert Tsat from PT source] | 26 bars(g) | [Insert Tsat from PT source] |

B) Understanding checks (model answers)

1. The PT relationship is refrigerant-specific. The same pressure gives different Tsat depending on refrigerant, so using the wrong PT table gives wrong SH/SC.

2. Pressure alone can mislead because operating conditions affect it: changing load/ambient/airflow; system may not be at steady‑state; inverter speed control alters pressures; measurement location and hose losses can influence readings.

3. Gauge pressure is measured relative to atmosphere; absolute pressure is measured relative to vacuum. A quick rule is bar(a) ≈ bar(g) + ~1 bar.

Practical mini-task (expected points)

Low side connects to suction/low-pressure service port; high side connects to discharge/high-pressure service port (where fitted) following manufacturer guidance.

Service port caps must be refitted as a secondary seal to prevent dirt/moisture ingress.