| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 3: Superheat & Subcooling Calculations

Key formulas

• Superheat (K) = T(suction line) − Tsat(suction pressure)

• Subcooling (K) = Tsat(discharge pressure) − T(liquid line)

Note: temperature differences in °C and K are numerically the same (e.g., 8°C difference = 8 K).

A) Worked example (complete the blanks)

Given: Tsat(suction) = 7°C, suction line T = 15°C

Superheat = ______ − ______ = ______ K

Given: Tsat(discharge) = 45°C, liquid line T = 39°C

Subcooling = ______ − ______ = ______ K

B) Practice table (use PT data or your Task 2 results for Tsat)

| Scenario | Tsat suction (°C) | Suction line T (°C) | Superheat (K) | Tsat discharge (°C) | Liquid line T (°C) | Subcooling (K) |
| --- | --- | --- | --- | --- | --- | --- |
| 1 |  | 18 |  |  | 40 |  |
| 2 |  | 14 |  |  | 37 |  |
| 3 |  | 22 |  |  | 42 |  |
| 4 |  | 16 |  |  | 35 |  |

| C) Interpretation prompts For each scenario above, circle the best description: • Superheat: LOW / OK / HIGH • Subcooling: LOW / OK / HIGH Then write ONE likely cause to check first (airflow / charge / restriction / controls). | D) Practical task Your tutor will demonstrate a pipe clamp probe. Write down THREE ways to reduce measurement error when measuring pipe temperature: 1) __________________________ 2) __________________________ 3) __________________________ |
| --- | --- |

Tutor guidance

Key formulas

Superheat (K) = T(suction line) − Tsat(suction pressure)

Subcooling (K) = Tsat(discharge pressure) − T(liquid line)

Note: temperature differences in °C and K are numerically the same.

A) Worked example (answers)

Given: Tsat(suction) = 7°C, suction line T = 15°C → Superheat = 15 − 7 = 8 K

Given: Tsat(discharge) = 45°C, liquid line T = 39°C → Subcooling = 45 − 39 = 6 K

B) Practice table (pre-filled calculation structure)

| Scenario | Tsat suction (°C) | Suction line T (°C) | Superheat (K) | Tsat discharge (°C) | Liquid line T (°C) | Subcooling (K) |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | [From PT] | 18 | 18 − Tsat(suction) | [From PT] | 40 | Tsat(discharge) − 40 |
| 2 | [From PT] | 14 | 14 − Tsat(suction) | [From PT] | 37 | Tsat(discharge) − 37 |
| 3 | [From PT] | 22 | 22 − Tsat(suction) | [From PT] | 42 | Tsat(discharge) − 42 |
| 4 | [From PT] | 16 | 16 − Tsat(suction) | [From PT] | 35 | Tsat(discharge) − 35 |

C) Interpretation guidance (marking points)

Low superheat → possible floodback risk/overfeeding/low airflow (check airflow first).

High superheat → possible underfeeding/low charge/restriction (confirm leak tightness and charge-by-mass requirement).

Low subcooling → possible undercharge/low load/measurement error.

High subcooling → possible overcharge/restriction/condenser issues.

D) Practical task – reducing pipe temperature error (model answers)

1. Clamp probe firmly on clean pipe surface and ensure good contact.

2. Insulate the probe from ambient air (wrap with insulation/foam).

3. Allow the reading to stabilise; avoid holding the pipe/probe.

4. Measure at manufacturer-recommended locations; keep location consistent.