| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 4: Completing a Commissioning Log (Case Study Simulation)

Scenario data (steady‑state)

Ambient: 18°C | Room: 26°C | Set point: 21°C | Mode: Cooling

Suction pressure: 6.0 bar(g) | Tsat suction: 6°C (from PT)

Discharge pressure: 19 bar(g) | Tsat discharge: 42°C (from PT)

Suction line temperature: 20°C | Liquid line temperature: 41°C

Indoor air on/off: 26°C → 20°C | Outdoor air on/off: 18°C → 30°C

Running current: Higher than expected at this load (no value given)

A) Complete the commissioning log

Commissioning log template (fill in)

| Field | Value | Field | Value |
| --- | --- | --- | --- |
| Ambient (°C) |  | Room temp (°C) |  |
| Set point (°C) |  | Mode |  |
| Suction pressure |  | Discharge pressure |  |
| Tsat @ suction (°C) |  | Tsat @ discharge (°C) |  |
| Suction line temp (°C) |  | Liquid line temp (°C) |  |
| Superheat (K) |  | Subcooling (K) |  |
| Indoor air on/off |  | Outdoor air on/off |  |
| Running current (A) | ________ (tutor demo) | Voltage (V) | ________ |
| Steady‑state confirmed? | Y / N | Notes |  |

B) Analysis & decision-making

1. Calculate superheat and subcooling for this scenario (show your working).

2. Which TWO additional pieces of information would you want before making any adjustments?

3. List THREE checks you would do before adjusting refrigerant charge.

4. Write one sentence explaining how you would document an adjustment (before/after evidence).

Tutor guidance

Scenario data (steady‑state)

Ambient: 18°C | Room: 26°C | Set point: 21°C | Mode: Cooling

Suction pressure: 6.0 bar(g) | Tsat suction: 6°C

Discharge pressure: 19 bar(g) | Tsat discharge: 42°C

Suction line temperature: 20°C | Liquid line temperature: 41°C

Indoor air on/off: 26°C → 20°C | Outdoor air on/off: 18°C → 30°C

Running current: Higher than expected at this load (tutor to demonstrate actual value)

A) Completed commissioning log (model)

| Field | Value | Field | Value |
| --- | --- | --- | --- |
| Ambient (°C) | 18 | Room temp (°C) | 26 |
| Set point (°C) | 21 | Mode | Cooling |
| Suction pressure | 6.0 bar(g) | Discharge pressure | 19 bar(g) |
| Tsat @ suction (°C) | 6 | Tsat @ discharge (°C) | 42 |
| Suction line temp (°C) | 20 | Liquid line temp (°C) | 41 |
| Superheat (K) | 14 | Subcooling (K) | 1 |
| Indoor air on/off | 26→20°C | Outdoor air on/off | 18→30°C |
| Running current (A) | [Enter measured A] | Voltage (V) | [Enter measured V] |
| Steady‑state confirmed? | Yes | Notes | Amps high vs expected at this load; investigate condenser airflow/charge/leak + verify measurements. |

B) Analysis & decision-making (model answers)

1. Superheat = 20 − 6 = 14 K; Subcooling = 42 − 41 = 1 K.

2. Two additional pieces of information: (1) manufacturer expected operating range (pressures, SH/SC, amps) for this ambient/load; (2) confirmed refrigerant type and total charge spec (including additional charge for line length).

3. Three checks before adjusting charge: check airflow (filters/coil/fan); check condenser cleanliness/fan operation and air recirculation; verify probe placement and insulation + PT conversion; perform leak check and review charge-by-mass requirement.

4. Documentation sentence: “Made one change, allowed system to re‑stabilise, then recorded before/after readings and final settings in the commissioning log.”