| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 5: Fault-Finding from Commissioning Data (Evidence-based decisions)

Instructions

For each mini-case, use the pattern of readings to select likely causes and next checks.

Important: these are learning scenarios. Real systems must be checked against manufacturer data and safe procedures.

A) Mini-cases

| Mini-case | Symptoms / readings (steady-state) | Most likely issue (choose 1) | First THREE checks you would do |
| --- | --- | --- | --- |
| A | SH high, SC low; room not reaching set point; suction pressure low | Undercharge / leak / restriction / airflow | 1) 2) 3) |
| B | SH low, SC high; head pressure high; amps high | Overcharge / condenser airflow / restriction / sensor error | 1) 2) 3) |
| C | Air ΔT small; pressures near expected; room reaches set point quickly; inverter ramps down | Low load / airflow too high / normal operation / charge issue | 1) 2) 3) |
| D | Suction pressure low; coil icing; SH low; filters visibly dirty | Low airflow / undercharge / metering fault / control error | 1) 2) 3) |

B) Reflection

1. Why is “add refrigerant” not a safe first response when performance is poor?

2. Explain why you should make only ONE change at a time during commissioning.

3. Give TWO examples of measurement error that could lead to a wrong diagnosis.

Practical task (role-play)

One learner is the engineer, one is the customer. Explain what measurements were taken and what the results mean in simple terms.

Tutor guidance

A) Mini-cases (model responses)

| Mini-case | Most likely issue (model) | First THREE checks (model) |
| --- | --- | --- |
| A | Undercharge/leak OR restriction (also verify airflow) | 1) Confirm steady-state/mode and PT conversion. 2) Check airflow (filters/coil/fan). 3) Leak check / compare to manufacturer expected values. |
| B | Condenser airflow issue OR overcharge OR restriction | 1) Check condenser coil/fan + recirculation. 2) Verify high-side pressure/temps and probes. 3) Confirm charge-by-mass spec and investigate restrictions. |
| C | Normal low-load/inverter behaviour OR airflow too high for load | 1) Confirm set point met and low load. 2) Review fan speed/airflow setting. 3) Compare to manufacturer part-load expectations. |
| D | Low airflow (primary) causing icing | 1) Clean/replace filters. 2) Check fan and coil condition; thaw then re-stabilise. 3) Re-measure; only then consider charge/leak if still abnormal. |

B) Reflection (model answers)

1. “Add refrigerant” is not a safe first step because it can be illegal/unsafe, hides the real fault (airflow/restriction/sensor error), and risks overcharge and high head pressure.

2. One change at a time allows cause-and-effect; multiple changes make it impossible to know what caused improvement or deterioration.

3. Measurement errors: uninsulated clamp probe influenced by ambient; air probe touching casing; wrong PT table for refrigerant; measuring during ramping/defrost; pressure at wrong point/hose losses.

Role-play (what “good” looks like)

Explain measurements in simple terms (pressures + temperatures show how the system works).

Explain what will be checked first (airflow and cleanliness), then how you will confirm improvement (before/after readings).

Give user-friendly advice (filters, set points, schedules, clear airflow).