| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 6: Commissioning Heat Pumps

Part 1: Leak testing plan

Write a step-by-step plan for how you would check for leaks during commissioning.

Include: visual inspection, high-risk points, direct methods (detector/bubbles), and what you would record.

Steps:

1) ________________________________________________________________

2) ________________________________________________________________

3) ________________________________________________________________

4) ________________________________________________________________

5) ________________________________________________________________

6) ________________________________________________________________

7) ________________________________________________________________

Part 2: What must be recorded? (tick all that apply)

Type of refrigerant and total quantity added/removed (kg)

Leak test method used (e.g., detector, bubbles, OFN pressure test)

Leak test result and any repairs made

Final control settings and set points at handover

Indoor/outdoor air on/off temperatures for each unit

Pressures and converted saturation temperatures (Tsat)

Running current at full load and near set point

Part 3: End-user controls test (practical checklist)

| Control/function | Pass / Fail / Notes |
| --- | --- |
| On/Off works and unit responds correctly |  |
| Mode changes (cool/heat/auto/fan) operate as expected |  |
| Set point changes produce a sensible response |  |
| Fan speed changes work (auto/low/med/high) |  |
| Timers/schedules (if fitted) operate correctly |  |
| Any lockouts/limits are explained (if fitted) |  |
| Fault/alarm indications are understood (what user sees) |  |
| Any integrated controls (e.g., BMS/remote sensor) are tested |  |

Part 4: Short questions

1. Explain how leaks affect energy efficiency (two sentences).

2. Why should the engineer record refrigerant added beyond the base charge?

3. What information would you give the user during handover to help them operate the system efficiently?

Tutor guidance

Part 1: Leak testing plan (example sequence)

1. Confirm site permissions and safe working (PPE, isolation where required).

2. Visual inspection for oil staining, damage, missing caps, vibration points.

3. Identify high-risk points: joints, valves/stems, seals, service ports, safety/operational device connections.

4. Use electronic leak detector methodically; confirm suspected leaks with bubble solution if appropriate.

5. If pressure testing required: recover refrigerant first; pressure test with OFN to specified pressure; never use oxygen.

6. Repair any leaks by competent person; repeat test to confirm repair.

7. Record method, locations, results, repairs, retest outcome, date/time, engineer details.

Part 2: What must be recorded? (correct selections)

All listed items should be recorded: refrigerant type/quantity; method; result/repairs; final settings; air on/off temps; pressures + Tsat; running current at different loads.

Part 3: End-user controls (pass criteria examples)

On/Off responds correctly; mode changes valid; set point changes affect operation; fan speeds change; timers/schedules run; alarms/indications explained; integrated controls (e.g., BMS) communicate correctly.

Part 4: Short questions (model answers)

1. Leaks reduce charge, lowering efficiency and capacity; the system runs longer and may operate at unfavourable pressures, increasing energy use.

2. Recording additional refrigerant beyond base charge supports correct total charge verification, compliance, and future fault-finding (e.g., identifying slow leaks).

3. Handover info: efficient set point advice; schedules/timers; filter maintenance; keeping doors/windows closed during cooling; maintaining clear airflow around units; what alarms mean and who to contact.