| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 1: Inspection Routine & Safety Boundaries

Scenario

You are about to inspect an air‑conditioning system during commissioning. Your aim is to spot abnormal operation, unexpected operational noise and any unsafe conditions.

A) Safety boundaries (tick when you can explain each point)

| Tick | Statement |
| --- | --- |
| ☐ | Why you must keep clear of moving fans/guards and never bypass safety devices. |
| ☐ | Why you must not touch electrical terminations or open electrical panels unless authorised/competent. |
| ☐ | Why hot surfaces should be assumed and checked safely. |
| ☐ | Stop/escalate triggers (burning smell, smoke, severe vibration, grinding contact). |
| ☐ | Why you must record evidence before cleaning/wiping anything (e.g., oil staining). |

B) Put the inspection steps in order

Write the numbers 1–7 to show the best order for a repeatable inspection routine:

___ Record evidence (what/where/when, photos, notes).

___ Make safe (follow procedures; isolate where required).

___ Decide action (monitor / fix / escalate).

___ Listen (hearing): noise patterns and changes.

___ Smell: burning/overheating/oil odours (treat seriously).

___ Observe (sight): leaks, wiring, loose panels, rub marks.

___ Feel (touch) carefully: vibration/temperature (no terminals/moving parts).

C) Short questions

1. What is the difference between a “clue” and a “confirmed fault” during inspection?

________________________________________________________________________________

________________________________________________________________________________

________________________________________________________________________________

2. Give three examples of evidence you could record during inspection.

________________________________________________________________________________

________________________________________________________________________________

________________________________________________________________________________

3. Why should you write down operating conditions (mode, fan speed, load) with your observations?

________________________________________________________________________________

________________________________________________________________________________

________________________________________________________________________________

Tutor guidance

Scenario (model)

Aim: spot abnormal operation, unexpected noise, and unsafe conditions using a repeatable inspection routine. Use senses to gather clues, then confirm safely.

A) Safety boundaries (model explanations)

Moving parts: fans can cause injury; guards prevent contact. Never bypass guards or interlocks. Keep hair/clothing/tools clear.

Electrical: terminations may be live even when the unit appears “off”. Only authorised/competent persons open panels or touch terminations.

Hot surfaces: discharge lines, compressor shells and motors can burn. Use “back of hand near surface” first and confirm with thermometer/IR.

Stop/escalate triggers: burning smell, smoke, arcing/buzzing from electrics, severe vibration, grinding/scraping contact, exposed wiring.

Evidence first: oil staining, rub marks and loose fixings are diagnostic clues—record location/photo before cleaning or tightening.

B) Inspection steps – correct order (answers)

Correct order (one acceptable sequence):

1) Make safe (follow procedures; isolate where required).

2) Observe (sight): leaks, wiring, loose panels, rub marks.

3) Listen (hearing): noise patterns and changes.

4) Feel (touch) carefully: vibration/temperature (no terminals/moving parts).

5) Smell: burning/overheating/oil odours.

6) Record evidence (what/where/when, photos, notes).

7) Decide action (monitor / fix / escalate).

C) Short questions – model answers

1. A clue is an observation from senses (e.g., oil stain, rattle, warm casing). A confirmed fault is verified using safe checks/instruments/manufacturer guidance (e.g., confirmed loose mount, confirmed rubbing fan, measured overheating).

2. Evidence examples: photo of oil staining; description of noise (type, when it occurs); sketch/notes of location; measured temperature with IR/thermometer; video/audio clip; record of fan speed/mode when symptom occurred.

3. Operating conditions affect what you observe. Noise and vibration can change with fan speed/load; temperatures depend on ambient and airflow; without conditions you cannot compare to “normal” or replicate the symptom.