| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 2: Using Your Senses to Identify Fault Clues

Practical activity: “Sensory walkaround” (classroom simulation)

Your tutor will set up stations (photos, props, short audio clips, or scenario cards). At each station, use your senses to spot clues. Then decide what you would do next.

A) Observation log (complete one row per station)

| Station | Sense used (sight/hearing/touch/smell) | What did you notice? (describe) | Likely cause (best guess) | Next action (monitor/fix/escalate) | Evidence to record |
| --- | --- | --- | --- | --- | --- |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| 4 |  |  |  |  |  |
| 5 |  |  |  |  |  |

B) Reflection questions

1. Which sense gave you the strongest clue today, and why?

________________________________________________________________________________

________________________________________________________________________________

________________________________________________________________________________

2. Give an example where your “best guess” could be wrong without further checks.

________________________________________________________________________________

________________________________________________________________________________

________________________________________________________________________________

3. List two safe ways to confirm a clue (without taking unsafe risks).

________________________________________________________________________________

________________________________________________________________________________

________________________________________________________________________________

Tutor guidance

A) Observation log – completed exemplar (5 stations)

Observation log (example answers)

| Station | Sense used | What noticed (describe) | Likely cause (best guess) | Next action | Evidence to record |
| --- | --- | --- | --- | --- | --- |
| 1 | Hearing | Rattle/buzz on casing, changes when panel pressed | Loose panel / missing fixing / resonance | Fix (tighten/secure) then re-check | Photo of missing screw; note: rattle stops when pressed; operating mode |
| 2 | Sight | Oil staining around joint near compressor base | Possible refrigerant leak path carrying oil | Escalate (leak check by competent person) | Photo; exact location; size/freshness of stain; date/time |
| 3 | Smell + sight | Hot electrical smell near indoor unit; slight browning on insulation | Overheating termination / wiring issue | Stop & escalate; isolate power per procedure | Smell description; photo of discolouration; time; mode |
| 4 | Touch (careful) + hearing | Noticeable vibration on outdoor panel; low-frequency rumble | Fan imbalance or loose mounts | Fix/Investigate, if severe escalate | Location map; video; note fan speed/load when strongest |
| 5 | Hearing | Squeal from fan/motor area increasing with speed | Worn/dry bearing or belt slip (if applicable) | Escalate if severe; investigate bearings safely | Note speed dependence; location; any temperature rise |

B) Reflection – model answers

1. Hearing often gives the strongest early clue because noise patterns change with speed/load and can be located without touching components.

2. Example: a whine might be normal inverter operation, or it might be resonance. Without comparing to baseline and checking mountings/guards, the “best guess” could be wrong.

3. Two safe confirmation methods: (1) change fan speed/set point (if allowed) and see if symptom changes; (2) visual inspection for rub marks/loose fixings; (3) confirm temperatures with IR/thermometer; (4) record and compare against manufacturer guidance.