| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 4: Vibration, Loose Panels, and High Temperatures (Practical Checks)

A) Vibration mapping (practical)

Your tutor will demonstrate vibration using a safe prop (e.g., a small vibrating device on a panel) or a video. Your job is to map where vibration is strongest and suggest likely causes.

Vibration mapping table

| Location where vibration is strongest | What might be causing it? | What would you check first? | What evidence would you record? |
| --- | --- | --- | --- |

B) High temperature clues

For each clue, write one likely cause and one safe next step.

Temperature clues table

| Clue | Likely cause (brief) | Safe next step |
| --- | --- | --- |
| Motor housing unusually hot |  |  |
| Cable insulation discoloured/brittle |  |  |
| Compressor area very hot + strong smell |  |  |
| Airflow appears blocked/restricted |  |  |

C) Loose panel “rattle test” (discussion)

1. How could gently pressing a panel (only if safe) help locate a rattle?

________________________________________________________________________________

________________________________________________________________________________

________________________________________________________________________________

2. List two reasons loose panels can be a safety issue, not just a noise issue.

________________________________________________________________________________

________________________________________________________________________________

________________________________________________________________________________

Tutor guidance

A) Vibration mapping – example completed responses

Vibration mapping table (example)

| Location where vibration strongest | Possible cause | First check | Evidence to record |
| --- | --- | --- | --- |
| Outdoor unit side panel near fan | Fan imbalance / loose guard / resonance | Inspect guard, fixings and clearances; check debris | Video of vibration; note fan speed; photo of loose fixing |
| Compressor base area | Loose mounts / failed isolator | Inspect mounts and bolts; look for movement | Photo of mount; note when vibration occurs (start/stop/steady) |
| Pipework at wall penetration | Pipe contact / lack of isolation | Check for contact points; add clearance/isolation (competent person) | Photo of rub mark; sketch location |
| Cable tray / conduit | Loose fixing causing buzz | Check tray fixings and clamps | Photo; note that vibration stops when supported |

B) High temperature clues – model answers

Temperature clues table (model)

| Clue | Likely cause (brief) | Safe next step |
| --- | --- | --- |
| Motor housing unusually hot | Overload, failing bearing, poor cooling airflow | Confirm with IR/thermometer; check airflow; escalate if overheating |
| Cable insulation discoloured/brittle | Overheating termination, loose connection, cable too near hot surface | Isolate and escalate; record location; do not touch terminations |
| Compressor area very hot + strong smell | Overheating/overload or electrical issue | Stop/isolate and escalate; record smell + conditions |
| Airflow appears blocked/restricted | Dirty coil, obstruction, recirculation | Check for obstructions/dirty filters/coil; record; correct if allowed |

C) Loose panel rattle test – model answers

1. If a rattle changes or stops when a panel is gently pressed (only if safe), it suggests the panel or its fixings are the noise source (resonance/looseness).

2. Safety issues: (1) panels/guards can detach and expose moving parts; (2) loose panels can cut cables/pipework through vibration, causing leaks or electrical faults.