| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 5: Inspection Record Sheet (What/Where/When/Evidence/Action)

Scenario (steady-state)

Scenario card from tutor: you will be given one of the following (or similar):
• Fan scraping increases with fan speed
• Burning smell near indoor unit + discoloured wiring
• Rattle on outdoor unit panel at start/stop
• Oil staining around a joint near compressor base

A) Complete the inspection record

Inspection record table

| Inspection area | Observation (describe) | Where exactly? | Operating conditions | Evidence (photo/reading/sketch) | Action (monitor/fix/escalate) |
| --- | --- | --- | --- | --- | --- |
| Compressor |  |  |  |  |  |
| Fans |  |  |  |  |  |
| Bearings |  |  |  |  |  |
| Panels/fixings |  |  |  |  |  |
| Vibration |  |  |  |  |  |
| Oil seepage/leaks |  |  |  |  |  |
| High temperatures |  |  |  |  |  |
| Wiring |  |  |  |  |  |

B) Short written response

1. Explain why “monitor / fix / escalate” is part of inspection.

________________________________________________________________________________

________________________________________________________________________________

________________________________________________________________________________

2. Give two examples of observations that should trigger immediate escalation.

________________________________________________________________________________

________________________________________________________________________________

________________________________________________________________________________

3. What extra information would help you decide whether something is normal or abnormal?

________________________________________________________________________________

________________________________________________________________________________

________________________________________________________________________________

Tutor guidance

Scenario used (example)

Burning smell near indoor unit + discoloured wiring; intermittent buzzing; area warm. Immediate safety escalation required.

A) Completed inspection record (example)

Inspection record table (completed example)

| Inspection area | Observation | Where exactly? | Operating conditions | Evidence | Action |
| --- | --- | --- | --- | --- | --- |
| Compressor | No abnormal noise noted | Outdoor unit | Cooling; steady-state | Note “no issue observed” | Monitor |
| Fans | Normal airflow; no scraping | Indoor fan | Fan speed: medium | Note | Monitor |
| Bearings | No squeal/rumble | Indoor motor area | As above | Note | Monitor |
| Panels/fixings | Panel secure | Indoor casing | As above | Photo (optional) | Monitor |
| Vibration | Minor normal vibration | Indoor casing | As above | Video (optional) | Monitor |
| Oil seepage/leaks | No oil staining seen | Around joints | As above | Photo if any | Monitor |
| High temperatures | Warm area near electrical section (do not touch terminals) | Indoor unit electrical enclosure area | Cooling; steady-state | IR reading if available; note “warm to touch nearby” | Escalate / isolate |
| Wiring | Discoloured insulation; possible overheating; buzzing sound | Near terminal area / cable entry | Cooling; steady-state; buzzing intermittent | Photo; smell description; time; operating mode | STOP/ISOLATE/ESCALATE |

B) Short written response – model answers

1. Inspection is used to decide what happens next: some issues can be monitored, some can be corrected safely, and some are safety-critical and require immediate escalation and isolation.

2. Immediate escalation examples: burning smell or smoke; arcing/buzzing from electrics; exposed/damaged wiring; grinding fan contact; severe vibration risking component failure.

3. Extra information: baseline “normal” sound/temperature for that model; manufacturer guidance; operating conditions (ambient/load); previous maintenance history; measured temps/amps (by competent person).