| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 2: Measure Fresh Air and Ventilation Effectiveness

K1.2 Air conditioning and ventilation in a modern economy

Scenario:

Measure ventilation performance and identify stale-air removal.

1. Airflow measurement at a ventilation grille

Use an anemometer

Record air velocity (m/s)

Measure size of the grille (m²)

Calculate airflow volume (m³/h)

Use the formula:

Airflow (m³/h) = Air velocity (m/s) × Area (m²)

|  | Air velocity | Size of grille | Airflow volume |
| --- | --- | --- | --- |
| Grille 1 |  |  |  |
| Grille 2 |  |  |  |
| Grille 3 |  |  |  |

2. Smoke test

Release a small amount of smoke near:

An extract grille

A supply vent

Observe and record:

Direction of airflow

How quickly the smoke is drawn in

Whether air is being extracted from the space correctly

Illustrate your findings here:

An extract grille

A supply vent

3. Indoor air quality reading

Where possible, take measurements of:

CO₂ (ppm)

Humidity (%)

Temperature (°C)

These readings help you understand why ventilation is required.

Tutor guidance

Question 1 – Airflow measurement at a ventilation grille

Check that learners:

- Take an accurate air velocity reading using an anemometer (m/s)

- Measure the grille free area (m²)

- Multiply them to calculate airflow in m³/s

- Convert m³/s to m³/h (× 3600)

Model example values (for guidance only):

| Grille | Air velocity (m/s) | Size of grille (m²) | Airflow volume (m³/h) |
| --- | --- | --- | --- |
| Grille 1 | 2.4 m/s | 0.12 m² | 2.4 × 0.12 × 3600 = 1037 m³/h |
| Grille 2 | 1.8 m/s | 0.10 m² | 1.8 × 0.10 × 3600 = 648 m³/h |
| Grille 3 | 3.1 m/s | 0.15 m² | 3.1 × 0.15 × 3600 = 1674 m³/h |

How airflow was calculated (example for Grille 1):

- Air velocity = 2.4 m/s

- Area = 0.12 m²

- Airflow (m³/s) = 2.4 × 0.12 = 0.288 m³/s

- Convert to m³/h → 0.288 × 3600 = 1037 m³/h

Question 2 – Smoke Test

Learners should observe:

- Whether smoke is drawn towards extract grilles

- Whether smoke is pushed away from supply vents

- Speed of movement (fast = good extraction)

- Any dead zones where air stagnates

- Sketch or describe results clearly

Model Answer:

- Extract Grille Observation

- Smoke moved quickly towards the grille, indicating good negative pressure.

- Smoke was fully drawn in within 2–3 seconds.

- This suggests the extract fan is operating effectively and stale air is being removed.

Supply Vent Observation

- Smoke was pushed away from the supply diffuser, showing good supply airflow.

- Air pattern was even and consistent, spreading across the room.

- No backflow or turbulence was seen that would indicate poor diffusion.

Question 3 – Indoor Air Quality Readings

Learners must take CO₂, humidity and temperature readings and explain what they mean.

If equipment is unavailable, realistic values are acceptable.

Model Answer:

| Measurement | Example Reading | Interpretation |
| --- | --- | --- |
| CO₂ (ppm) | 760 ppm | Acceptable indoor concentration (below 1000 ppm = good ventilation). |
| Humidity (%) | 48% | Within comfort range (40–60%). Good for health and comfort. |
| Temperature (°C) | 21.5°C | Comfortable indoor temperature. Suggests HVAC is controlling conditions well. |

Explanation for Learners:

- CO₂ shows how well fresh air is entering the room. Lower values = better ventilation.

- Humidity helps prevent mould (too high) or dry air (too low).

- Temperature affects comfort and HVAC load.