| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 4 – Filter Condition and Pollution Removal

K1.2 Air conditioning and ventilation in a modern economy

Objective:

Learners will investigate how filters help improve air quality.

Tutor guidance

- How to lead, supervise, and support learners through each of the four filter‑related activities

- What to prompt, observe, and check for

Evidence learners produce:

- Notes on filter condition

- Airflow readings

- Explanation of how filter blockage impacts ventilation

Question 1: Examine clean vs dirty filters

- Help learners visually identify the difference between a clean and a contaminated filter.

- Link filter condition to airflow, efficiency, and indoor air quality.

### Tutor actions

- Provide a selection of clean and intentionally dirty/used filters (e.g., panel filters, pleated filters, HEPA-style training filters).

- Ask learners to inspect appearance, noting:

  - Colour changes (white/clean vs grey/brown)

  - Dust buildup in pleats or mesh

  - Blocked or clogged sections

  - Physical damage (tears, deformities)

### Tutor prompts

- What do you think has caused the dirt buildup?

- Where in a building might this level of dirt come from?

- How do you think a dirty filter affects airflow?

### Safety notes

- Ensure learners do not shake dirty filters.

- Encourage use of gloves and masks when handling heavily contaminated filters.

Question 2: Identify what each filter type removes (dust, pollen, smoke, VOCs)

- Build understanding of the purpose of different filter grades.

- Reinforce that not all filters remove the same pollutants.

### Tutor actions

Prepare a small set of filter types, such as:

- Coarse filters (G3–G4): dust, large particles

- Fine filters (F7–F9): pollen, smaller particulates

- HEPA/activated carbon filters: smoke, allergens, VOCs, odours

Ask learners to label or match filters to what they remove.

### Tutor prompts

- Which filter would be most effective during pollen season?

- Why might an activated carbon filter be used in a workshop or kitchen?

- Which filter would you expect to find in a hospital or clean room?

Question 3: Fit a filter correctly into an AC training unit

- Ensure learners can safely and correctly install filters.

- Emphasise airflow direction and sealing.

Tutor actions

- Demonstrate the correct method first:

- Isolate power to the unit.

- Remove access panels safely.

- Show the airflow direction arrow on the filter.

- Ensure the filter seats firmly without gaps.

- Observe learners installing their filters.

Tutor prompts

- Check the airflow direction—does the arrow match the airflow path?

- Is the filter sitting squarely in the frame?

- What might happen if the filter is not sealed properly?

Tutor checks

- No visible gaps where air could bypass the filter.

- Panels are re-secured correctly.

- Learners do not over-tighten fixings.

## Question 4: Record airflow before and after filter change (using an anemometer)

- Show the relationship between filter condition and airflow.

- Provide hands-on experience with measuring instruments.

### Tutor actions

- Demonstrate correct anemometer use:

  - Positioning at supply grille

  - Holding steady for accurate readings

  - Using multiple readings to find an average

- Ask learners to:

  - Measure airflow before filter change.

  - Replace the filter.

  - Measure airflow after the change.

  - Compare results.

### Tutor prompts

- What difference do you see between old and new filter readings?

- Why does airflow generally increase with a clean filter?

- Would this change affect energy consumption?

### Expected learning

- Dirty filters restrict airflow → lower performance

- Clean filters restore proper airflow → improved efficiency and air quality

Question 5: How blocked filters reduce:

•   Fresh-air intake

•   Cooling performance

•   Air quality

## a. How blocked filters reduce fresh-air intake

- A blocked filter restricts airflow, making it harder for fresh outdoor air to enter the system.

- The ventilation system has to work harder, often pulling in less fresh air than required.

- Reduced intake leads to higher CO₂ levels, increased humidity, and a “stuffy” indoor environment.

- Less fresh air means poor dilution of pollutants, causing the indoor environment to feel stale.

## b. How blocked filters reduce cooling performance

- Restricted airflow across the cooling coil results in less air being cooled and circulated.

- The cooling system becomes less efficient, taking longer to reach set temperatures.

- Reduced airflow may cause the coil to freeze, further decreasing performance and increasing energy use.

- The system runs for longer periods, leading to higher energy consumption and unnecessary wear.

## c. How blocked filters reduce air quality

- Pollutants such as dust, pollen, and microbes are not captured effectively when airflow is low.

- Contaminants accumulate in the air, leading to poor indoor air quality.

- Can trigger allergies, respiratory issues, and discomfort.

- Poor filtration allows dirt buildup inside ducts and equipment, contributing to odours and hygiene problems.