| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 5 – Knowledge Check Questions

K1.2 Air conditioning and ventilation in a modern economy

Tutor answers:

1. Describe two different uses of air conditioning.

Tutor answer (model):

Comfort cooling: Keeps people comfortable by controlling temperature, humidity and air movement in occupied spaces (e.g. classrooms, offices, shops, homes).

Process cooling: Controls temperature and sometimes humidity for equipment or processes (e.g. server rooms/data centres, manufacturing lines, medical storage, CNC machines, laser cutters), where stable conditions protect products or machinery rather than people.

Accept also: close control AC, chillers for production lines, precision rooms/labs.

________________________________________

2. Explain the difference between cooling for human comfort and cooling for industrial processes.

Tutor answer (model):

Comfort cooling targets human comfort ranges (approx. 20–24 °C, moderate humidity), with some flexibility and a focus on IAQ (filters, ventilation).

Process cooling targets strict, non-negotiable setpoints (often narrow bands, e.g. ±1 °C or tighter) to protect products/equipment; reliability and continuous operation are prioritised over occupant comfort. Air may be unoccupied, and ventilation is added only when needed.

Key contrast: purpose (people vs. process), tolerance (wide vs. tight), controls (simple vs. precision), consequences (discomfort vs. product/equipment failure).

________________________________________

3. What is ventilation?

Tutor answer (model):

Ventilation is the planned movement and exchange of air—bringing fresh outdoor air in and removing indoor air (exhaust)—by natural means (windows/vents) or mechanical systems (fans, AHUs/HRVs). Its role is to dilute contaminants and to manage temperature and humidity, keeping indoor air healthy.

4. How does ventilation remove stale or harmful air?

Tutor answer (model):

Ventilation dilutes and displaces pollutants by supplying clean outdoor air and extracting indoor air. This reduces CO₂, odours, moisture, fine particles, and gases (VOCs). Mechanical systems maintain required air changes per hour (ACH) and pressure differences so polluted air is carried to the exhaust and replaced with filtered fresh air.

________________________________________

5. Why is fresh air required in occupied spaces?

Tutor answer (model):

To maintain safe CO₂ levels, limit odours, control humidity (reducing mould/dust mites), and dilute airborne contaminants (allergens, aerosols, VOCs). Adequate fresh air supports health, comfort, and concentration and helps meet building/education guidance for IAQ.

Credit if learners reference observations: lower CO₂/odours when outdoor air increased.

________________________________________

6. What did your smoke test reveal about airflow direction?

Tutor answer (model):

At extract grilles/fans: Smoke was drawn into the grille → confirms extraction path toward the duct/fan and out of the building.

At supply diffusers: Smoke was pushed away and dispersed into the room → confirms supply airflow.

Any dead spots/backflow indicate poor balancing, blocked filters, or incorrect fan direction.

Award higher marks where learners link their observation to the system diagram or note speed/response time.

________________________________________

7. Based on your measurements, what happens when ventilation is reduced?

Tutor answer (model):

Air velocity/flow rate at grilles drops (calculated m³/h falls).

CO₂ rises, humidity may rise, and odours linger – the room feels ‘stale’.

Temperature stratification can increase and smoke clears more slowly.

If extraction only is running (or blocked supply), spaces may go negative pressure, drawing in unfiltered air from gaps.

Look for data: before/after CO₂ (ppm), air velocity (m/s), airflow (m³/h), humidity (%).

________________________________________

8. How did the filter condition affect airflow?

Tutor answer (model):

A dirty/blocked filter increases resistance (pressure drop), so airflow decreases at the same fan speed. This reduces fresh air intake, weakens extraction, and can harm cooling performance and IAQ. After fitting a clean filter, measured airflow increases and distribution improves.

Evidence to credit: anemometer readings before vs. after, visible dust loading, notes on filter type/orientation and proper sealing.

For all task worksheets:

These sources support the technical content provided:

CIBSE (Chartered Institution of Building Services Engineers) — Ventilation and air conditioning fundamentals

HVACR Basics – ASHRAE (American Society of Heating, Refrigerating and Air Conditioning Engineers) — Definitions of comfort cooling and process cooling

UK Health & Safety Executive (HSE) — Guidance on indoor air quality and ventilation requirements

Building Regulations (UK) Part F — Ventilation and fresh air requirements