| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 6: Improving Ventilation

K1.2 Air conditioning and ventilation in a modern economy

Objective:

Learners will measure ventilation performance and identify stale-air removal.

Equipment:

- Anemometer

- Smoke pen or smoke tube

- CO₂ meter (if available)

- Humidity & temperature

- PPE

Tutor guidance

- Demonstrate how to hold the anemometer 10–20 cm from the grille.

- Explain the difference between supply and extract airflow.

- Show how to calculate the grille free area (e.g., width × height).

- Model the formula:

- Airflow (m³/h) = air velocity (m/s) × area (m²) × 3600

What learners should demonstrate

- Consistent measurement technique

- Accurate recording of velocity

- Correct calculation using the formula

- Awareness of any variation between grilles

Common misconceptions to address

- Learners forgetting to convert to m³/h

- Measuring too close to the grille, causing turbulence

- Using gross grille dimensions instead of free area

Smoke Test (Air Direction & Extraction Quality)

Tutor guidance

- Explain why smoke shows airflow patterns.

- At the extract grille, prompt learners to observe:

Direction (towards the grille?)

- Strength (how quickly smoke moves?)

- Any “dead zones” with little movement

At the supply vent, prompt learners to observe:

- Whether smoke is pushed away

- Spread of air across the room

- Any turbulence or bouncing

What learners should notice

- If extract is effective, smoke is drawn in rapidly.

- If supply is effective, smoke moves outward smoothly.

- Slow or stagnant smoke = poor ventilation.

Safety note

- Ensure smoke pens are used with good ventilation and correct PPE.

- Remind learners not to place their faces near grilles.

Indoor Air Quality Measurements (If Equipment Available)

Tutor guidance

- Ask learners why CO₂ is used as an indicator of ventilation rate.

- Discuss acceptable ranges:

- CO₂: ideally under 1000 ppm

- Humidity: 40–60%

- Temperature: 20–22°C typical indoor comfort

Relate poor IAQ readings to real-world issues (comfort, productivity, health).

What learners should conclude

- Higher CO₂ = insufficient fresh air

- Low humidity = dry and uncomfortable

- High humidity = risk of condensation and mould

- Temperature readings may show if HVAC is compensating for occupancy levels