| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 1: Thermodynamics & Temperature

K1.3 Scientific principles: temperature scales, sensible/latent heat, superheat & subcooling

Instructions: Show all working. Use SI units. Round answers to 2–3 significant figures unless specified.

Questions

Q1. Convert the following temperatures:

(a) 21 °C to K

(b) 295 K to °C

(c) −5 °C to K

(d) 310 K to °C

Show all working and give answers with correct units.

Given:

Use K = °C + 273.15

Q2. Air at 20 °C is warmed to 27 °C at a mass flow rate of 0.85 kg/s. Assuming c_p (air) = 1.005 kJ/(kg·K), calculate the sensible heat rate in kW.

Show all working and give answers with correct units.

Q3. A domestic dehumidifier condenses 1.2 kg of water per hour... If h_fg = 2,400 kJ/kg, estimate latent heat removal rate (kW).

Show all working and give answers with correct units.

Q4. An evaporator outlet temperature (actual) is 9 °C; saturation at suction is 5 °C. Determine the superheat.

Show all working and give answers with correct units.

Q5. A condenser outlet is 34 °C; condensing saturation is 40 °C. Determine the subcooling.

Show all working and give answers with correct units.

Q6. AHU cools 27 °C DB, 50% RH to 14 °C sat, m=1.6 kg/s. Assume h_in=55, h_out=38 kJ/kg; compute total kW, sensible kW (c_p=1.005), SHR.

Show all working and give answers with correct units.

Tutor guidance

Q1 – Answer

(a) 294.15 K

(b) 21.85 °C

(c) 268.15 K

(d) 36.85 °C

Q2 – Answer

Q = 0.85×1.005×7 = 5.98 kW (~6.0 kW)

Q3 – Answer

m=1.2 kg/h=0.000333 kg/s; Q=0.000333×2400=0.80 kW

Q4 – Answer

4 K

Q5 – Answer

6 K

Q6 – Answer

Q_total=1.6×(55−38)=27.2 kW; Q_sens=1.6×1.005×13=20.9 kW; SHR=0.77