| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 3: Psychrometrics & Commissioning Calculations

Instructions: Show all working. Use SI units. Round answers to 2–3 significant figures unless specified.

Questions

Q1. Name two instruments to measure moisture in air and what they measure.

Q2. AHU 1.9 kg/s: 26 °C 50% RH → 13 °C sat. Assume h_in=51, w_in=0.0100; h_out=36, w_out=0.0092. Find total kW, moisture removal (kg/h & L/h), sensible kW (c_p=1.005), SHR.

Show all working and give answers with correct units.

Given:

ρ_water=1000 kg/m³

Q3. Room sensible heat via airflow: 2.2 m³/s at 14 °C supply; 24 °C return; ρ=1.2 kg/m³; c_p=1.005. Find kW.

Show all working and give answers with correct units.

Q4. ADP estimate: out 12.5 °C at 95% RH, BF=0.12, in 27 °C. T_ADP≈T_out − BF×(T_out − T_in).

Show all working and give answers with correct units.

Q5. On the schematic chart, indicate where 100% RH lies and lower RH lines.

Tutor guidance

Model answers (one of many possible solution methods).

Q1 – Answer

Sling psychrometer (WB/DB); Hygrometer (RH)

Q2 – Answer

Total 28.5 kW; 5.47 kg/h ≈ 5.47 L/h; sensible 24.8 kW; SHR ≈ 0.87

Q3 – Answer

≈26.6 kW

Q4 – Answer

≈14.2 °C (illustrative)

Q5 – Answer

100% RH = saturation curve boundary; lower RH below it