| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 5: Psychrometrics, Charts & Apps

Use a psychrometric chart or a reliable app. Take atmospheric pressure as 101.3 kPa unless stated.

1. Find RH and humidity ratio

At DBT = 26 °C and WBT = 18 °C: use a chart/app to determine:

(i) relative humidity (%),

(ii) humidity ratio (kg/kg dry air).

2. Properties at 22 °C, 50% RH

Find:

(i) humidity ratio,

(ii) specific volume (m³/kg),

(iii) moist air enthalpy (kJ/kg).

Then estimate sensible cooling from 22 °C to 18 °C at constant humidity ratio for 0.5 kg/s of dry air.

3. Air mixing

Mix 0.4 kg/s of air at 30 °C, 60% RH with 0.2 kg/s at 20 °C, 40% RH. Using a chart/app, estimate mixed-state enthalpy and DBT.

4. Refrigerant comparator

Using a refrigerant comparator app, find saturation temperature at 8 bar(g) for R‑410A and for R‑32. Record both values and comment which has the higher T_sat at the same pressure.

Extension

1) Using a chart/app, determine the **sensible heat ratio (SHR)** for cooling air from 26 °C, 50% RH to 18 °C supply air at ~95% RH at 0.6 kg/s dry air. Show how you obtained h and w values.

2) A room sensible load is 5.2 kW with a supply airflow of 0.90 m³/s. Estimate the supply air temperature difference (ΔT). Use ρ=1.2 kg/m³, c_p=1.005 kJ/kg·K.

3) Using a refrigerant comparator, at 35 °C find saturation pressure for R‑32 and R‑410A. Comment on which has the higher pressure at the same temperature.

Tutor guidance

Note: exact values vary by chart/app and barometric pressure. Give full credit for consistent method within ±5%.

Typical answers at 101.3 kPa:

Question 1
DBT 26 °C, WBT 18 °C → RH ≈ 45–55%; humidity ratio w ≈ 0.008–0.010 kg/kg.

Question 2
22 °C, 50% RH → w ≈ 0.0083 kg/kg, v ≈ 0.86 m³/kg, h ≈ 43 kJ/kg. Sensible cooling for 0.5 kg/s from 22→18 °C: Q ≈ 0.5×1.005×4 ≈ 2.0 kW.

Question 3
Mixing by mass/enthalpy balance: ṁ_total=0.6 kg/s; h_mix ≈ (0.4 h₁ + 0.2 h₂)/0.6. Expect DBT ≈ 26–27 °C (indicative).

Question 4
Comparator: R‑410A vs R‑32 at 8 bar(g): tutors to accept app-based values and reasoning.

Extension
1) SHR = sensible/total. Sensible per kg ≈ 1.005×(26−18) ≈ 8.0 kJ/kg. Total = h_in − h_out from your app; expect SHR ≈ 0.75–0.85. Credit correct method ±5%.

2) ṁ = 1.2×0.90 = 1.08 kg/s ⇒ ΔT ≈ 4.8 K.

3) Accept app values; typically, R‑32 has higher saturation pressure than R‑410A at the same temperature.