| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 4: Heat Transfer & Capacity Calculations

Instructions: Show all working. Use SI units. Round answers to 2–3 significant figures unless specified.

Questions

Q1. Wall with R-values: compute U and steady heat loss for 18 m², 22→5 °C.

Show all working and give answers with correct units.

Q2. Coil convection: h=35 W/m²K, A=1.8 m², ΔT=9 K. Find Q.

Show all working and give answers with correct units.

Q3. Supply 1.7 kg/s: 26→14 °C. Sensible kW (c_p=1.005).

Show all working and give answers with correct units.

Q4. 9 m suction line adds 1.5 K superheat; m=0.12 kg/s; c_p,vap=0.90. Heat pick-up?

Show all working and give answers with correct units.

Q5. Ventilation 0.6 m³/s at 30 °C into 24 °C stream; ρ=1.2; c_p=1.005. Sensible load kW?

Show all working and give answers with correct units.

Q6. Secondary refrigerant (30% glycol): remove 65 kW from 12→7 °C; ρ=1035; c_p=3.9. Mass and volume flow?

Show all working and give answers with correct units.

Tutor guidance

Model answers (one of many possible solution methods).

Q1 – Answer

U≈0.362 W/m²K; Q≈111 W.

Q2 – Answer

Q≈567 W.

Q3 – Answer

≈20.5 kW.

Q4 – Answer

≈162 W.

Q5 – Answer

≈4.35 kW.

Q6 – Answer

m≈3.33 kg/s; V≈3.22 L/s.