| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 2: Heat Transfer

Air Conditioning Temperature Conversion Questions

1. Celsius → Kelvin

An AC technician measures the return air temperature in a building as 18°C.

What is this temperature in Kelvin?

Answer

18°C → Kelvin

K=C+273

18+273=291" K"

Answer: 291 K

________________________________________

2. Celsius → Kelvin

The outdoor condenser unit is operating at a coil temperature of 42°C.

Convert this temperature to Kelvin.

Answer

42°C → Kelvin

42+273=315" K"

Answer: 315 K

________________________________________

3. Kelvin → Celsius

A refrigerant line inside a commercial AC system is measured at 295 K.

What is the temperature in Celsius?

Answer

295 K → Celsius

C=K-273

295-273=22^∘ "C"

Answer: 22°C

________________________________________

4. Kelvin → Celsius

During a system diagnostic, the evaporator coil temperature is recorded as 265 K.

What is the temperature in Celsius?

Answer

265 K → Celsius

265−273 = –8°C

Answer: –8°C

Heat Transfer Practice Problems

Problem 1 — Sensible Heat (Air Cooling)

Air enters an evaporator at 28°C and leaves at 18°C.

The airflow rate is 0.6 m³/s.

Calculate the cooling rate (kW).

Solution

ΔT=28-18=10^∘ C

HVAC formula:

Q ̇=1.2⋅V ̇⋅ΔT

Q ̇=1.2⋅0.6⋅10=7.2" kW"

Answer: 7.2 kW of cooling

________________________________________

Problem 2 — Sensible Heat (Heating Air)

Air is heated from 15°C to 30°C with an airflow of 0.4 m³/s.

Find the heating rate.

Solution

ΔT=30-15=15^∘ C

Q ̇=1.2⋅0.4⋅15

Q ̇=7.2" kW"

Answer: 7.2 kW of heating

________________________________________

Problem 3 — Latent Heat (Dehumidification)

An evaporator removes 0.01 kg/s of water vapour from the air.

Latent heat of vaporisation L=2,500,000" J/kg".

Solution

Q ̇=mL

Q ̇=0.01×2,500,000

Q ̇=25,000" W"=25" kW"

Answer: 25 kW of latent cooling

________________________________________

Problem 4 — Conduction Heat Loss (Wall)

A cold room wall has:

Area: 12 m²

Thickness: 0.1 m

Thermal conductivity k=0.04" W/m\cdotpK"

Temperature difference across wall: 20°C

Solution

Q ̇=kA ΔT/d

Q ̇=0.04×12×20/01

Q ̇=0.48×200=96" W"

Answer: 96 W of heat transfer

________________________________________

Problem 5 — Temperature Change Using Basic Formula

A refrigerant line carrying 2 kg/s of fluid is cooled by 5°C.

Specific heat c=1,400" J/kg\cdotp°C" .

Solution

Q ̇=mcΔT

Q ̇=2×1400×5

Q ̇=14,000" W"

Answer: 14 kW

________________________________________

Problem 6 — Mixed Sensible & Latent Cooling

An AC system cools air from 27°C to 20°C while also removing 0.004 kg/s of moisture.

Airflow is 0.5 m³/s.

What is the combined cooling?

Solution

Sensible Cooling

ΔT=27-20=7^∘ C

Q ̇_s=1.2⋅0.5⋅7=4.2" kW"

Latent Cooling

Q ̇_l=0.004×2,500,000=10,000" W"=10" kW"

Total Cooling

Q ̇_total=4.2+10=14.2" kW"

Answer: 14.2 kW (combined cooling)

________________________________________

Problem 7 — Combined Heat Gain

A small office has the following loads:

People: 1.5 kW

Lighting: 0.9 kW

Equipment: 1.2 kW

Solar gain: 2 kW

Calculate the total cooling load needed.

Solution

Q ̇_total=1.5+0.9+1.2+2

Q ̇_total=5.6" kW"

Answer: 5.6 kW cooling required

________________________________________

Problem 8 — Airflow Required

A classroom needs 6 kW of sensible cooling.

The expected temperature drop across the evaporator is 10°C.

Calculate the required airflow (m³/s).

Formula

Q ̇=1.2⋅V ̇⋅ΔT

Solution

6=1.2⋅V ̇⋅10

6=12V ̇

V ̇=6/12=0.5" m³/s"

Answer: 0.5 m³/s airflow required

________________________________________

Problem 9 — Condensate Production (From Latent Load)

An AC system provides 6 kW of latent cooling.

How much condensate is produced in litres per hour?

Solution

m ̇_water=6000/2,500,000=0.0024" kg/s"

Convert to L/h:

0.0024×3600=8.64" L/h"

Answer: 8.64 litres of condensate per hour

________________________________________

Problem 10 — Condensate Rate from Moisture Removal

The evaporator removes 0.005 kg of water every second.

How many litres per hour is this?

Solution

1 kg of water = 1 L

0.005" kg/s"×3600=18" L/h"

Answer: 18 L/h