| Learner name: |  | Class: |  | Date: |  |
| --- | --- | --- | --- | --- | --- |

Task 5: DSR/DSM practical: schedule an HVAC system to support the grid

Learning outcome

Explain DSR (short-term response) and DSM (broader management).

Use a tariff/carbon profile to plan load shifting.

Propose HVAC actions that maintain comfort and safety constraints.

Practical task A: Plan a daily schedule (25–30 min)

Your tutor will provide a 24-hour table of electricity price and/or carbon intensity.

Assume the building needs 40 kWh of cooling per day (chiller electricity).

You have an ice tank that can store 15 kWh of ‘cooling’.

Create a schedule that decides when to: (1) run chiller normally, (2) charge ice tank, (3) discharge ice tank.

Goal: reduce cost and/or carbon while staying within comfort limits.

| Time block | Price/Carbon (from tutor) | Action (run/charge/discharge) | kWh moved | Reason |
| --- | --- | --- | --- | --- |

Practical task B: Comfort & constraints check (10–15 min)

List at least 5 constraints that limit how much you can shift HVAC demand.

For each constraint, write one control strategy to stay safe (e.g. max temp band, min ventilation rate).

| Constraint | Why it matters | Control / mitigation |
| --- | --- | --- |

Output: short justification

Write a 150–200 word explanation of your schedule and how it supports the grid.

________________________________________________________________________________

________________________________________________________________________________

________________________________________________________________________________

________________________________________________________________________________

________________________________________________________________________________

________________________________________________________________________________

________________________________________________________________________________

________________________________________________________________________________

Tutor guidance

Use as a model answer + marking guidance. Accept equivalent correct wording.

Key idea (what to look for)

Schedule shifts part of cooling demand away from peak price/carbon periods.

Uses ice tank: charge when price/carbon is low (often midday solar or overnight off-peak); discharge during peak (late afternoon/early evening).

Maintains comfort constraints: setpoint bands, minimum ventilation/IAQ, maximum discharge rate, protect plant limits.

Example schedule pattern (generic)

10:00–16:00 (high PV / lower carbon): run chiller + charge ice tank up to capacity.

16:00–19:00 (peak): reduce chiller run and discharge ice tank to cover part of load.

Night (if tariff supports): optional top-up charging if needed and allowed.

Constraints – acceptable answers

Thermal comfort (temperature/humidity limits)

Indoor air quality (minimum ventilation rates)

Occupancy patterns/exams/IT room criticality

Equipment limits (compressor cycling, max ramp rates)

Noise restrictions, frost protection, legionella/DHW safety where relevant

Metering/controls/communications reliability

Note: price/carbon table is tutor-provided. Mark the logic and method; accept different time windows if justified by the provided profile.

Marking guidance (suggested /12)

| Criterion | What good looks like | Marks |
| --- | --- | --- |
| Schedule quality | Clear actions with kWh moved; aligns to provided price/carbon profile. | 5 |
| Constraints | 5+ realistic constraints with mitigation strategies. | 4 |
| Justification | Coherent explanation linking to grid support + comfort. | 3 |