## Slide 1
Occupational Specialism: Plumbing & Heating Engineering
K1.7 Plumbing and heating systems
Indirect cold water systems

## Slide 2: Starter
Warm-up:
Recall what you learned about direct cold water systems.
Sketch a quick comparison between a direct system and what may be involved in an indirect system, even if you are unsure.

## Slide 3: Objectives
You should be able to:
Explain the principles of indirect cold water supply
Identify layouts and component positions
Recognise valves used in indirect systems
You might also be able to:
Understand storage requirements and hygiene concerns
Evaluate advantages and disadvantages

## Slide 4: Introduction to indirect systems
Indirect cold water systems store water in a cistern, usually located in the loft or roof space. The storage cistern feeds most outlets such as baths, WCs, and basins, while the kitchen cold tap is kept on the mains for potable water.
This arrangement ensures a reserve of water is always available, even if the mains supply is interrupted. However, because much of the system operates at low pressure, flow rates can be poor.
The cistern also requires regular maintenance to prevent contamination. Despite these drawbacks, indirect systems are common in older housing and larger properties.

## Slide 5: Principle of indirect supply
Storage cistern in loft feeds most outlets.
Kitchen tap remains on mains.
Reserve supply available during mains interruptions.
Outlets supplied at low pressure.
Requires more components than direct systems.
Question: Why is the kitchen cold tap always left on the mains supply in an indirect system?

## Slide 6: Indirect system layout
Rising main enters and fills storage cistern.
Float-operated valve controls water level.
Overflow/warning pipes required.
Distribution pipes supply WCs, baths, basins.
Kitchen cold remains on mains (for drinking water – fluid category 1).

## Slide 7: Key components – indirect system
230–250 litre storage cistern fitted with BS 1212 part 2 float-operated valve
22mm or 28mm cold feed to hot water cylinder
22mm cold distribution
A
B
B
C
D
D
E
E
F
Stop valve
Drain valve
Service valve
Gate valve
Washing machine valve
Isolation valve
Notes: Diagram drawn by author

## Slide 8: Student task – sketch layout
Students: draw an indirect system, including rising main, cistern, float valve, overflow, warning pipe, and cistern-fed outlets.
Once complete, share and review sketches to identify missing parts.
Tutor: provide a model sketch for comparison, reinforcing correct layout design.

## Slide 9: Cold water storage cistern
The cold water storage cistern is the heart of an indirect system. It is usually located in a loft space, raised above outlets to create pressure by gravity.
The cistern is fitted with a float operated valve to control filling, an overflow pipe to discharge excess water safely, and a warning pipe to signal faults.
Cisterns must be covered, insulated, and constructed from approved materials to prevent contamination. Regular maintenance is required to avoid dirt, insects, or bacterial growth. Storage capacity must be sized correctly to meet household demand. 500mm clearance is required above the cistern for maintenance.

## Slide 10: Water fittings regulations
Cisterns must be made of approved materials.
Covers required to prevent contamination.
Insulation to prevent freezing or undue warming.
Warning and overflow pipes mandatory.
Float valves must prevent backflow (suitable air gap arrangements).
WRAS-approved components required.

## Slide 11: Warning pipes & overflows
Cisterns must have a warning system for overflow; a warning pipe is standard, with alternatives allowed by the water undertaker.
Combined overflow/warning pipes may be used for cisterns below 1000 litres.
Pipes should slope downward and must not discharge into another cistern.

## Slide 12: Hygiene concerns
Because water is stored, hygiene is a key issue in indirect systems. Cisterns must always be covered to prevent insects, dust, or vermin entering.
Insulation prevents temperature fluctuations that could encourage bacterial growth (legionella bacteria).
Pipes should be arranged to minimise stagnation, and outlets should be flushed if unused.
Hygiene risks are one of the main disadvantages of indirect systems.

## Slide 13: Demonstration – cistern components
Tutor: show students a model cistern or photographs of real installations. Components such as the float valve, warning pipe, and overflow are identified.
Students: discuss how each part contributes to safe operation and compliance with regulations.

## Slide 14: Component – valves
Float-operated ball valve (controls filling).
Stop valve on rising main to cistern.
Service valves on branches to outlets.
Non-return valves where required by regs.
Drain-offs for maintenance.
Question: Why must a cold water storage cistern always have a warning pipe fitted?

## Slide 15: Student task - common valves
Students: research what each of the following valves looks like, and their purpose.
Stop valve
Drain valve
Service valve
Gate valve
Washing machine valve
Isolation valve.
Notes: Tutor to show examples online or physical examples in class once students have completed the task.

## Slide 16: Pipework distribution
Outlets supplied from cistern: baths, basins, WCs.
Kitchen tap always on mains.
Gravity pressure depends on vertical distance.
Larger pipes may be needed for adequate flow.
Insulation required in loft spaces.

## Slide 17: Advantages of indirect systems
Reserve water supply in case of mains failure.
Quieter operation compared to direct systems.
Reduced strain on pipework and fittings.
Multiple outlets can run simultaneously without major drop in flow.
Provides reasonable head of pressure for hot water cylinder supply.

## Slide 18: Disadvantages of indirect systems
Requires more space for cistern.
Higher installation cost.
Risk of water stagnation if unused.
Regular maintenance needed for cistern hygiene.
Poor pressure.
Question: What is your preference? Think of your property – which system is more suitable?

## Slide 19: Pressure and flow
Water pressure depends on cistern height above outlets.
1 metre head = approximately 0.1 bar of pressure.
Low-pressure outlets is often poor for showers.
Booster pumps may be required.
Larger cisterns provide greater reserve.
Question: Why might a shower on the top floor of a house have poor flow in this system?

## Slide 20: Demonstration – loft installation
Tutor: show photos or diagrams of a loft installation.
Students: identify insulation, pipe routing, and overflow arrangements. Suggest improvements and highlight possible issues.
Discussion includes the risks of freezing in winter and how proper insulation prevents bursts.
Tutor: highlight safe access and maintenance requirements.

## Slide 23: Multiple cisterns
When large amounts of water are needed but space is limited, cisterns of the same size and capacity can be linked together. If linked incorrectly, especially for drinking water supply, water stagnation can occur, reducing quality.
The number of linked cisterns should be kept to a minimum.
To prevent stagnation, connections must promote good water flow through each cistern. This can be done by keeping cistern volumes small for quick water turnover, linking cisterns in parallel, placing inlets and outlets at opposite ends, and using delayed-action float-operated valves to reduce stratification.

## Slide 24: Knowledge check 1
What component controls cistern filling?
Why is the kitchen cold tap always on mains?
What is the purpose of an overflow pipe?
Name one advantage of an indirect system.
Name one disadvantage of an indirect system.

## Slide 25: Knowledge check 1 – answers
Float-operated valve.
Ensures potable water is available.
Safely discharges excess water.
Provides reserve supply.
Risk of stagnation/poor pressure.

## Slide 26: Cistern materials
Most new cisterns are made from plastics like polyethylene, polypropylene, or glass-reinforced plastic (GRP). Polypropylene is preferred because it is lightweight, strong, hygienic, corrosion-resistant, and flexible, making it easy to manoeuvre through roof spaces.
Cisterns come in square, rectangular, or circular shapes, usually in black to prevent algae growth.
Their bases must be fully supported to avoid damage from their flexibility. Pipe connection holes should be made with a hole saw, not heated copper, as heat can weaken the plastic and cause cracks.
Joints between cistern walls and fittings should use plastic or rubber washers. Galvanised steel cisterns were once common but are prone to corrosion.
Notes: Discuss old asbestos cisterns as a concern in older properties.

## Slide 27: Activity – component handling
Tutor provides sample filling valves and float valves.
Students identify each part and explain its role.
Compare traditional vs modern valve designs.
Discuss failure signs and common faults (worn diaphragm washer on BS1212/2).
Reinforce regulation compliance.

## Slide 28: Case study – freezing risk
In a cold winter, a poorly insulated loft caused a cistern to freeze, cutting off supply to all outlets except the kitchen cold tap.
What steps should have been taken to prevent this incident?

## Slide 29: Control of dead legs
Keep branches short to outlets.
Avoid unused pipe runs.
Flush outlets regularly if unused (chlorinate if a significant risk is posed).
Prevents stagnation and contamination.
Requirement under regulations.
Question: Why do dead legs create a hygiene risk in stored water systems?

## Slide 30: Discussion – indirect vs direct
Tutor: lead a class discussion comparing direct and indirect systems.
Students: consider water quality, pressure, space requirements, and system complexity.
In groups, list when one system would be preferred over the other.

## Slide 31: Student task – sketch comparison
Draw direct and indirect systems side by side.
Include stop valves, service valves, drain-offs.
Mark cistern, float valve, overflow in indirect.
Highlight kitchen tap differences.
Share with peers for feedback.

## Slide 32: Maintenance – indirect systems
Inspect cistern lid, vent, and overflow.
Clean cistern periodically to remove debris.
Check float valve operation (a common fault is a worn diaphragm washer on type 2 float valves leading to water hammer).
Flush outlets to maintain water quality.
Ensure insulation is intact and effective.
Question: What risk can occur if a cistern lid is missing or damaged?

## Slide 33: Pressure testing
Before use, indirect systems must be tested for leaks and performance.
The cistern is filled, and all outlets are checked for adequate flow. Joints and fittings must be inspected for leaks, and valves tested for operation.
Records should be kept of the commissioning test. Proper testing prevents costly faults and ensures compliance.
It also builds confidence in the system’s long-term reliability.

## Slide 34: Knowledge check 2
Where is the cold water storage cistern usually located?
What does the warning pipe do?
Why is insulation required in loft spaces?
Which regulation governs fittings?
What type of pipe material must be approved?

## Slide 35: Knowledge check 2 – answers
In the loft/roof space.
Shows faults and overfilling.
Prevents freezing and bursts.
Water Fittings Regulations 1999.
WRAS-approved copper or plastic.

## Slide 36: Case study – freezing risk
A neglected cistern without a cover became contaminated with insects and debris. Occupants reported poor taste and odour in the water.
Discuss what should have been done earlier to prevent contamination.
What steps need to be taken to return this system to good working order and conform to regulations?

## Slide 37: Documentation
Water Supply (Water Fittings) Regulations 1999.
Building Regulations Part G – Sanitation, Hot Water Safety and Water Efficiency.
WRAS approval for fittings and materials.
BS EN standards for installation.

## Slide 38: Summary of advantages
Reserve water available.
Quieter than direct systems.
Good for large properties.
Lower stress on mains.
Compatible with vented hot water cylinders.

## Slide 39: Summary of disadvantages
Risk of stagnation and contamination.
Low water pressure.
Requires loft space and insulation.
More components, more cost.
Maintenance required more frequently.

## Slide 40: Final knowledge check
Above what capacity do cisterns require a separate overflow and warning pipe?
Why are inlets and outlets often installed at opposite ends in large cisterns?
Give one advantage of an indirect system.
Give one disadvantage of an indirect system.
What process is used to ensure cisterns and dead legs are free from legionella?

## Slide 41: Final knowledge check – answers
1000 litres
To avoid the risk of stagnation
Performance unaffected by household usage
Low pressure, higher installation cost and risk of water stagnation if unused
Chlorination

## Slide 42: Summary
You should be able to:
Explain the principles of indirect cold water supply
Identify layouts and component positions
Recognise valves used in indirect systems
You might also be able to:
Understand storage requirements and hygiene concerns
Evaluate advantages and disadvantages

## Slide 43
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.