## Slide 1
Occupational Specialism: Plumbing & Heating Engineering
K1.7 Plumbing and heating systems
K1.8 Components used in plumbing and heating systems
Open vented heating systems

## Slide 2: Starter
Warm-up:
In pairs, list some features or components you would find in an open vented system.
How can you find out what system you have at home?

## Slide 3: Objectives
You should be able to:
Describe the roles of open vent pipe, cold feed, expansion pipe and F&E cistern
State the requirements for vent pipe installation
Explain the function of two-pipe systems and the circulator
You might also be able to:
Compare one-pipe and two-pipe layouts
Identify and sketch open vented system layouts

## Slide 4: Open vented heating systems
Open vented heating systems are traditional hot water and heating arrangements commonly found in older properties. They rely on a feed and expansion (F&E) cistern, cold feed pipe, and open vent pipe to maintain system pressure and safety.
The cistern supplies water to the system and accommodates expansion as water heats.
The open vent pipe provides a pathway for air and steam to escape safely.
Although modern sealed systems are now widely used, understanding open vented systems is essential for diagnosing, servicing, and upgrading heating installations.

## Slide 5: The open vent pipe
The open vent pipe provides a safety outlet from the heating system into the feed and expansion cistern. Its main purpose is to allow air to escape and prevent dangerous build-up of pressure.
It also acts as a safeguard against overheating, as steam or hot water can escape via the vent. Correct installation is essential to ensure it can perform its role effectively.

## Slide 6: Role of the cold feed and expansion pipe
Supplies fresh water to the heating system.
Maintains system pressure at safe level.
Allows for expansion when water is heated.
Works in conjunction with open vent pipe.
Connects to the feed and expansion cistern.
Question: What happens if the cold feed pipe is blocked or incorrectly fitted?

## Slide 7: Feed and expansion cistern
The F&E cistern is usually located in the loft space above the heating system. It provides a small reserve of water and maintains system water level.
It allows expansion and contraction to take place safely as water heats and cools.
The cistern must have a close-fitting lid, screened overflow, and be insulated to prevent contamination or freezing.

## Slide 8: Role of the cold feed and expansion pipe
Minimum internal diameter of 22mm.
Termination at least 450mm above cistern water level.
Must rise vertically with no restrictions.
Positioned to discharge safely into cistern.
Connected close to the boiler flow for safety.
Question: Why is it important that the open vent rises vertically without restrictions?

## Slide 9: Safety role of the open vent
The open vent is the last line of defence against system overpressure. If safety devices or thermostats fail, the vent allows excess water and steam to escape harmlessly into the cistern.
Incorrect installation can result in pumping over, water loss, or even scalding risks.
Following dimensional requirements ensures safe and effective operation.

## Slide 10: Cold feed pipe requirements
Usually 15mm minimum diameter.
Connects into system near open vent for combined safety.
Provides make-up water automatically.
Must not be fitted with isolation valves.
Correct siting prevents air locks.

## Slide 11: Relationship between vent, cold feed, and cistern
The cold feed, expansion pipe, and open vent must be arranged together to ensure proper circulation and safety. The feed and vent connections must be no greater than 150mm apart. They connect into the primary circuit near the boiler to maintain water level and release air.
This arrangement ensures the system remains topped up and expansion is safely managed. An air separator can also be installed to provide flexibility to the installer when configuring the vent and feed connections.
Incorrect positioning can lead to poor circulation, corrosion, or unsafe conditions.

## Slide 12: One-pipe system
In a one-pipe system, all radiators are connected in series on a single circuit. Water flows through each radiator in turn before returning to the boiler.
This results in radiators nearer the boiler heating more effectively than those further away. Although cheaper to install, it is less efficient and rarely used in modern systems.

## Slide 13: Two-pipe heating system layout
Separate flow and return pipes.
Each radiator connected across both.
Water flows evenly through each radiator.
Provides consistent heating.
Reduces temperature drop across system.
Question: Why does a two-pipe system provide more even heating compared to a one-pipe system?

## Slide 14: Comparing two-pipe and one-pipe systems
Two-pipe: balanced heating, greater efficiency.
One-pipe: uneven heating, higher losses.
Two-pipe: easier to control with thermostatic valves.
One-pipe: lower initial installation cost.
Two-pipe: modern standard for central heating.
Question: Which system offers better energy efficiency, and why?

## Slide 15: The circulator
The circulator, or pump, drives water around the system to ensure even heating. In older systems, gravity circulation was used, but modern systems rely on pumps.
The circulator ensures that heated water reaches all radiators quickly and returns to the boiler for reheating. Pump speed can often be adjusted to suit system design.
Modern circulators are electronically controlled and energy efficient. They adjust speed automatically based on system demand. This reduces noise, energy use, and pumping over risk. Correctly selected circulators improve comfort and efficiency while extending system life.

## Slide 16: Location of the circulator
Normally fitted on return near boiler.
May be factory fitted in modern boilers.
Positioned to provide even distribution.
Must be accessible for servicing.
Should be sized to system capacity.
Question: Why is the circulator usually fitted on the return pipe?

## Slide 17: Tutor activity – system layouts
At this stage, the tutor should show students diagrams and live examples of one-pipe and two-pipe open vented systems.
Students should identify flow, return, open vent, cold feed, and F&E cistern connections.
Comparing layouts visually reinforces the theoretical understanding of component roles and flow paths.

## Slide 18: Student sketch task
Sketch a two-pipe open vented heating system.
Include boiler, F&E cistern, vent, cold feed, and radiators.
Label flow and return connections.
Mark circulator position.
Compare with example diagrams provided.

## Slide 19: Advantages of two-pipe systems
Two-pipe systems deliver more consistent heating and greater energy efficiency. They allow independent control of radiators, often with thermostatic valves.
Heat distribution is balanced, avoiding complaints of cold rooms.
They are also easier to maintain, as individual radiators can be isolated without affecting the rest of the system.

## Slide 20: Tutor demonstration – component parts
Show live circulator.
Demonstrate F&E cistern and vent connection.
Highlight open vent pipe termination.
Compare real-world parts to schematic drawings.
Encourage students to handle components.

## Slide 21: Midpoint knowledge check
What is the minimum diameter of an open vent pipe?
What role does the cold feed play in a system?
How does a two-pipe system improve radiator performance?
Why is the circulator vital in modern systems?
What is the function of the F&E cistern?

## Slide 22: Midpoint knowledge check – answers
22mm minimum diameter.
Provides make-up water and maintains system level.
By giving each radiator its own flow/return path.
To circulate heated water effectively around the system.
Provides reserve water and expansion space.

## Slide 23: Pumping over issues
Pumping over occurs when the circulator forces water up the open vent into the cistern. This wastes energy, causes water loss, and introduces oxygen into the system.
Oxygen promotes corrosion and sludge build-up. Pumping over is usually caused by incorrect pipework layout or excessive pump speed.

## Slide 24: Correcting pumping over
Ensure vent and feed are correctly positioned.
Adjust pump speed.
Rebalance system pipework.
Insulate cistern and pipework.
Service circulator as required.
Question: What is the main consequence of oxygen entering a heating system through pumping over?

## Slide 25: Safety features of open vented systems
The open vent and cistern provide inherent safety features. Excess heat or pressure is released harmlessly into the cistern.
Water level is automatically maintained, reducing risk of dry firing.
While less efficient than sealed systems, open vented systems are simple, reliable, and safe if installed correctly.

## Slide 26: F&E cistern maintenance
Keep lid in place to prevent contamination.
Ensure overflow is screened and operational.
Check insulation to prevent freezing.
Inspect for leaks or corrosion.
Flush and clean periodically.

## Slide 27: Tutor activity – identifying faults
Show students faulty cistern lid.
Demonstrate poor vent positioning.
Discuss symptoms of pumping over.
Encourage students to diagnose faults from diagrams.
Compare correct vs incorrect installations.

## Slide 28: One-pipe vs two-pipe summary
While one-pipe systems were once common due to lower cost, modern heating uses two-pipe layouts almost exclusively. They allow more even heating, independent control, and improved efficiency.
Two-pipe systems integrate better with modern controls such as thermostatic valves and smart heating systems.

## Slide 29: Practical sketching activity
Students refine two-pipe sketches.
Add flow arrows.
Ensure vent and feed shown correctly.
Tutor feedback on accuracy.
Share and compare designs in class.

## Slide 30: Knowledge check – circulator
What is the main purpose of a circulator?
Where is it usually fitted in the system?
How can circulators reduce energy use?
What problem occurs if pump speed is too high?
Why must circulators be accessible?

## Slide 31: Knowledge check – circulator – answers
To move heated water around the system.
On the return pipe near the boiler.
By adjusting speed to match demand, reducing wasted pumping energy.
Pumping over into cistern, causing air entry and corrosion.
For maintenance and replacement access.

## Slide 32: Open vented systems
Although sealed systems are now more common, open vented systems are still used in older properties and where roof space is available. They are particularly suited to solid fuel boilers, where uncontrolled heat input requires an open vent for safety. Understanding their operation remains essential for service and repair work.
Common faults include pumping over, blocked cold feed, leaking cisterns, and air locks. Air locks reduce circulation and radiator performance. Blocked feeds can cause systems to run dry, risking boiler damage. Diagnosing and correcting these faults is a key skill for heating engineers.

## Slide 33: Importance of system balancing
Even in two-pipe systems, balancing is essential. By adjusting lockshield valves, flow is distributed evenly across radiators.
Without balancing, closer radiators overheat while distant ones remain cold.
Balancing improves comfort and efficiency.
Notes: Note to tutor: More information on system balancing found here - https://www.vaillant.co.uk/advice/heating-tips/home-advice/how-to-balance-radiators/

## Slide 34: Health and safety considerations
Working on open vented systems requires awareness of hot water, confined spaces, and loft access. PPE must be worn when inspecting cisterns.
Safe ladder use and insulation checks are essential.
Spillage from vents or cisterns must be contained to avoid slips or scalds.

## Slide 35: Midpoint knowledge check 2
State the minimum height of vent pipe above cistern water level.
What is pumping over?
Why are vent and cold feed usually fitted close together?
What role does the F&E cistern play in safety?
Name one advantage of a two-pipe system.

## Slide 36: Midpoint knowledge check 2 – answers
450mm above cistern water level.
Water being forced up the vent into the cistern by the pump.
To ensure circulation safety and prevent air locks.
Acts as a reservoir, expansion space, and safety backup.
More efficient, balanced heating.

## Slide 37: Student sketch review
Students present their labelled two-pipe open vented sketches.
Tutor highlights accuracy in vent, feed, and circulator placement.
Sketches should match schematic diagrams provided earlier in session.

## Slide 38: Summary table – key components
Component | Function | Requirement
Open vent | Releases air/steam | 22mm min, 450mm above water
Cold feed | Maintains level | Near vent, no isolation
F&E cistern | Provides reserve water | Lid, overflow, insulation
Circulator | Drives water flow | Positioned on return

## Slide 39: System identification task
Tutor shows range of live components.
Students identify open vent pipe, cold feed, cistern.
Identify circulator and flow/return.
Compare findings with diagrams.
Correct any misconceptions.

## Slide 40: Final knowledge check
What protects against system overpressure in open vented systems?
Why do cisterns need screened overflows?
Which system provides better radiator performance?
What symptom suggests a blocked cold feed?
Why is balancing important?

## Slide 41: Final knowledge check – answers
The open vent pipe into the F&E cistern.
To prevent insects or debris entering.
Two-pipe systems.
Radiators not filling, boiler dry firing, circulation problems.
Ensures even heating and efficiency across all radiators.

## Slide 42: Summary
You should be able to:
Describe the roles of open vent pipe, cold feed, expansion pipe and F&E cistern
State the requirements for vent pipe installation
Explain the function of two-pipe systems and the circulator
You might also be able to:
Compare one-pipe and two-pipe layouts
Identify and sketch open vented system layouts

## Slide 43
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.