## Slide 1
Occupational Specialism: Plumbing & Heating Engineering
K1.7 Plumbing and heating systems
K1.8 Components used in plumbing and heating systems
Unvented hot water principles

## Slide 2: Starter
Warm-up:
Why must unvented hot water systems include multiple safety devices?

## Slide 3: Objectives
You should be able to:
Explain the principles of unvented hot water systems
Identify key components and their functions
You might also be able to:
Understand safety devices and three-tier protection
Describe installation and regulatory requirements

## Slide 4: What is an unvented hot water system?
Unvented hot water systems are mains-pressure storage cylinders that supply hot water without the need for a cold water storage cistern. They operate directly from the mains, providing strong flow at outlets and removing the need for a feed cistern.
Unlike vented systems, they rely on expansion vessels and safety valves to control pressure.
Their design offers improved performance but requires strict adherence to regulations to ensure safety.

## Slide 5: Advantages of unvented systems
High pressure hot water supply.
Balanced pressure at all outlets.
No cold water storage cistern required.
Less risk of contamination.
More flexible siting of cylinder.

## Slide 6: Regulations
Unvented hot water systems in the UK must comply with Part G3 of the Building Regulations.
Only trained and certified installers may fit or service them. Installers must notify the local Building Control or operate under a Competent Person Scheme.
British Standards such as BS 8558 (Complementary guidance to BS EN 806) and BS EN 12897 provide detailed technical guidance.
Compliance ensures safety and legal accountability.

## Slide 7: Safety principle – three-tier protection
Control thermostat (normal operation).
Overheat thermostat (secondary cut-out).
Pressure/temperature relief valve (ultimate safeguard).
Each tier provides backup to the previous and prevents overheating, overpressure, and cylinder rupture.
Question: Why is a three-tier system of safety devices essential in unvented hot water systems?

## Slide 8: Control thermostat
The control thermostat regulates the cylinder temperature during normal operation, typically set around 60°C.
This ensures water is hot enough to prevent bacterial growth but not excessively high. It cycles the heat source on and off to maintain steady conditions. If the control thermostat fails, backup devices must intervene.
Correct calibration and maintenance are essential for reliable operation.

## Slide 9: Overheat thermostat
Operates if control thermostat fails.
Cuts power to immersion heater or shuts boiler input.
Usually set around 85–90°C.
Manual reset may be required.
Prevents dangerous overheating of stored water.
Question: Why is this device not self-resetting?

## Slide 10: Pressure Relief Valve (PRV)
The pressure relief valve is a key safety device that opens when system pressure exceeds its set limit, often 6 bar. It prevents excessive pressure build-up that could damage the cylinder.
The valve must discharge to a tundish and then via a visible, safely terminated pipe.
Regular inspection is needed to ensure it remains free of scale or blockage.

## Slide 11: Temperature and Pressure Relief Valve (TPRV)
Combines pressure and temperature protection.
Opens if cylinder exceeds ~90°C or ~7 bar.
Final safeguard against catastrophic failure.
Must discharge via tundish to safe location.
Mandatory on all unvented systems.
Question: Why must a TPRV discharge pipe terminate in a visible and safe location?

## Slide 12: Expansion vessel
Unvented cylinders use an expansion vessel to accommodate water expansion when heated. The vessel contains an air-filled diaphragm that compresses as water volume increases.
This prevents unwanted pressure rise during normal operation. If the vessel loses charge, pressure relief valves may activate unnecessarily.
Regular checks and recharging are therefore essential parts of maintenance.

## Slide 13: Tundish
Small viewing device in discharge pipework.
Provides visible indication of water passing through valves.
Acts as an air gap to prevent backflow.
Must be installed in accessible, visible location.
Positioned between valve and discharge pipe.
Question: What would be the outcome if a tundish is not installed between the D1 & D2?

## Slide 14: Discharge pipework
Discharge pipework from safety valves must be correctly sized and installed to safely carry away hot water. It should be short, direct, and fall continuously to the outlet point.
Approved Document G3 for unvented hot water systems outlines two sections for discharge pipework: D1 and D2. D1 is the high-temperature pipe from the pressure relief valve to a visible tundish, while D2 carries discharge from the tundish to a safe external termination point, ensuring visible and safe dispersal of any water release.
The termination must be visible and located where escaping water will not cause damage or injury. Compliance with G3 guidance ensures safety and regulatory acceptance.
Notes: Taken from page 24 of Building Regs G3

## Slide 15: Midpoint knowledge check
What regulation governs unvented hot water in the UK?
Name the three tiers of protection.
At what temperature does the overheat thermostat activate?
What is the role of the expansion vessel?
Why must a TPRV discharge visibly?

## Slide 16: Midpoint knowledge check – answers
Part G3 of Building Regulations.
Control thermostat, overheat thermostat, TPRV.
Around 85–90°C.
To absorb expansion of heated water and prevent excess pressure.
To provide a visible warning of a system fault.

## Slide 17: Installation requirements
Unvented cylinders must only be installed by competent, certified engineers. Installation requires correct siting, adequate discharge pipe routes, and compliance with manufacturer’s instructions.
Cylinders should be located where discharge won’t cause damage and where access for service is straightforward. Notification to Building Control is mandatory unless installed under a Competent Person Scheme.
All installation details must be logged in the Benchmark logbook.

## Slide 18: Key installation checks
Adequate mains pressure and flow rate.
Correctly sized pipework.
Proper location for expansion vessel.
Safe discharge route for TPRV.
Benchmark certification completed.
Question: Why must the installer check mains pressure before fitting an unvented system?

## Slide 19: Commissioning process
Commissioning ensures the system operates safely and efficiently from the outset. It includes filling the cylinder, checking for leaks, testing safety devices, and recording system pressures and temperatures.
Expansion vessels must be pre-charged, and thermostats tested for proper function.
The installer must complete Benchmark documentation and explain the system to the end user.

## Slide 20: End-user instructions
Show location of isolation valves.
Demonstrate function of tundish and discharge pipe.
Explain normal operating pressures and noise levels.
Advise on annual servicing requirements.
Provide Benchmark logbook for records.
Question: Why should end-users be shown the tundish during commissioning?

## Slide 21: Servicing requirements
Annual servicing is essential for safety and regulatory compliance. Checks include testing all thermostats, operating safety valves, recharging the expansion vessel, and inspecting discharge pipework.
Scale control measures, such as immersion element descaling, may be required in hard water areas.
Service results must be recorded in the Benchmark logbook, providing a compliance record for both client and water authority.

## Slide 22: Common faults
Dripping tundish from faulty PRV or vessel.
Expansion vessel losing charge.
Thermostat malfunction.
Scale build-up on immersion heaters.
Discharge pipe incorrectly terminated.
Question: What could cause a tundish to drip continuously during normal operation?

## Slide 23: Fault diagnosis
Diagnosing faults requires a methodical approach. Continuous tundish discharge points to pressure or expansion issues. No hot water may indicate thermostat or immersion element failure.
Excessive noise could result from scale, incorrect installation, or pressure fluctuations.
Engineers should use service history, flow charts, and manufacturer’s instructions to guide diagnosis.

## Slide 24: Safety and functional devices recap
Control thermostat – normal operation.
Overheat thermostat – secondary cut-out.
PRV – pressure protection.
TPRV – pressure and temperature protection.
Expansion vessel – absorbs water expansion.
Tundish – visible warning and air gap.
Question: Which safety device provides the final safeguard against catastrophic failure?

## Slide 25: Legal requirements
Only engineers holding a G3 qualification may install or service unvented systems. Work must comply with Part G3 and must be either notified to Building Control or carried out under a Competent Person Scheme.
Non-compliance may result in enforcement action, invalid insurance, or safety hazards.
This legal framework ensures unvented systems remain safe and reliable.

## Slide 26: Case study – faulty installation
This installation was discovered after a certification request from a customer selling their property.
What essential component is missing from the installation?
What other issues can you spot?
Discuss in pairs and then feed back to your tutor.

## Slide 27: Case study
The main issue is the lack of tundish or D2 pipework providing a route for discharged water from the appliance.
There are several installation issues (such as the exposed electrical components and inadequate clipping), but the lack of tundish and D2 would result in damage to the property.
The installation was non-compliant, and the installer was fined. This highlights the importance of following regulations and manufacturer’s instructions.

## Slide 28: Secondary circulation
Some unvented systems incorporate secondary hot water circulation for rapid delivery to outlets. This requires careful design to avoid excessive heat loss and maintain water hygiene.
Additional safety devices may be required, and return pipework must be insulated.
Pumps should be controlled by timers or thermostats to balance efficiency with performance.

## Slide 29: Final knowledge check
What document must installers complete at commissioning?
Name three common service checks.
What does a tundish indicate?
Who is legally allowed to install unvented systems?
Why is secondary circulation sometimes added?

## Slide 30: Final knowledge check – answers
Benchmark logbook.
Test valves, recharge expansion vessel, check thermostats.
Discharge of water, showing system fault.
G3-qualified engineers.
To provide faster hot water at outlets.

## Slide 31
Safety and functional devices
Device | Function | Normal Operation Setting | Backup / Safety Role | Maintenance Needs
Control thermostat | Maintains cylinder temperature for normal use | ~60°C | Prevents overheating in daily use | Test annually for correct operation
Overheat thermostat | Cuts power if control stat fails | ~85–90°C | Secondary protection against overheating | Test reset function during service
Pressure Relief Valve (PRV) | Releases water if pressure rises above design limit | ~6 bar | Prevents overpressure during fault | Check for leaks; operate annually
Temperature & Pressure Relief Valve (TPRV) | Opens if temperature >90°C or pressure >7 bar | 90°C / 7 bar | Final safeguard against cylinder rupture | Test discharge annually; ensure free movement
Expansion Vessel | Absorbs expansion of heated water | Varies by system size | Prevents unnecessary PRV activation | Check charge pressure annually; recharge if needed

## Slide 32
Safety and functional devices
Device | Function | Normal Operation Setting | Backup / Safety Role | Maintenance Needs
Tundish | Provides visible discharge warning and air gap | Always dry in normal use | Alerts user to safety valve discharge | Inspect visually; keep accessible
Discharge Pipework | Carries discharged water to safe location | Short, direct fall, visible termination | Prevents scalding/damage from hot water | Check sizing and termination during service
Check Valves | Prevent backflow into mains | N/A | Ensures system integrity | Inspect for leaks; replace if faulty
Strainer/Filter | Removes debris from incoming supply | Inline with cold feed | Protects valves and controls | Clean/replace as required
Benchmark Logbook (documentation) | Records installation, commissioning, servicing | Completed at handover | Legal proof of compliance | Keep updated with each service

## Slide 33: Summary
You should be able to:
Explain the principles of unvented hot water systems
Identify key components and their functions
You might also be able to:
Understand safety devices and three-tier protection
Describe installation and regulatory requirements

## Slide 34: Exit quiz
What regulation covers unvented hot water systems?
What are the three tiers of protection?
Why is the tundish both a warning and a safeguard?
How often should an unvented cylinder be serviced?
What qualification must an installer hold to work legally on these systems?
Notes: Tutor to give answers at the end of the session.

## Slide 35
Any questions?
Copyright in this document belongs to and is used under licence from the Department for Education, © 2025.
‘T-LEVELS’ and ‘T Level’ are registered trademarks of the Department for Education.
WJEC is authorised by the Department for Education to develop and deliver this T Level Technical Qualification.
WJEC operates in England under the name Eduqas which is a registered trademark of WJEC.